Pressure & Level Measurement Solutions

Pressure Gauges Dial Indicating Differential Sanitary Digital

Pressure & Level Transducers & Transmitters

Industrial OEM

Hazardous Location Sanitary

Pressure Switches Options & Accessories

A

t NOSHOK, we pride ourselves on being innovators in the industry by continually offering the latest technology and measurement solutions, and providing the best customer support in the marketplace.

Established in 1967, NOSHOK was one of the first companies to offer liquid filled pressure gauges. We also took a bold step by backing our quality gauges with an extended 3-year warranty. That unwavering standard of quality has endured for

over 50 years, and as we have expanded our product offering we continue to provide industry-leading warranties. NOSHOK also leads the industry as one of the first companies to offer corrosion-resistant zinc nickel plating standard on our carbon steel valves.

We have the capacity to put together special requirements which are so often hard to find. If you do not find what you need in this catalog, chances are we can still put a solution together.

NOSHOK is committed to providing excellence on every level. Thank you for choosing NOSHOK products.

Jeff N. Scott President

NOSHOK Corporate Headquarters

Your Single Source Instrumentation Company

NOSHOK is a member and actively supports:

NOSHOK is an ISO 9001:2015 registered company.

WARRANTY INFORMATION

NOSHOK’s Five Year Warranty applies to our 1000 and 1100 Series differential gauges.

Our Three Year Warranty applies to our 300, 500, 502, 660, 760, and 900 Series liquid filled gauges; 10 Series liquid filled

sanitary gauges; 1000 Series digital gauge; 100, 200, 300, 612, 613, 615/616, 621/622, 623/624, 625/626, 627, 640, 650, 660 and 800 Series transmitters & transducers; 11 Series sanitary transmitters, and 500, 800 Series electronic switch products.

Our One Year Warranty applies to our 100, 200, 400, 402, 640, 740, and 800 Series dry gauges; 10 Series dry sanitary gauges; 100, 200, 300 and 400 Series mechanical switch products, and 628 Series intrinsically safe hammer union transmitter.

NOSHOK guarantees all products to be free from defects in material and workmanship, to remain within catalogued accuracy specifications, and to operate within the catalogued performance specifications. These products must be operated within the catalogued environmental and application parameters. Determination of failure will be made by NOSHOK, Inc.’s equipment and personnel or a certified test facility specializing in this type of evaluation. Instrument failures determined to be caused by over-range, incompatibility with environment or product media and abuse will not be considered under this warranty. NOSHOK, Inc. will, at its discretion, repair or replace the instrument without cost to the customer.

Limitations which apply are: Bourdon tube pressure gauges must be used within their calibrated maximum range to prevent damage. Pressure gauges must be operated within the following working pressure limits: Dynamic pressure application, 60% of the dial range; Static pressure applications, where no sharp fluctuations occur, 90% of the dial range. The gauges must be operated within specified ambient temperature ranges.

CAUTION:

Operating conditions including, but not limited to, system pressure, media compatibility and ambient conditions must be considered when selecting gauges and accessories, improper selections and use of gauges could possibly cause gauge failure and lead to possible property damage or personal injury. Refer to the American National Standard ASME B40.1 for the correct selection and use of dial indicating gauges.

T A B L E O F C O N T E N T S

DIAL INDICATING PRESSURE GAUGES

ABS & Steel Case, Dry:

100 SERIES	6-9

Low Pressure Diaphragm:

200 SERIES	10-13

Brass Case, Liquid Filled:

300 SERIES	14-17

All Stainless Steel, Dry & Liquid Filled:

400/500 SERIES	18-21

All Stainless Steel, Dry & Liquid Filled, Extreme High Pressure:

402/502 SERIES	22-25

Process:

600/700 SERIES	26-27

Precision Test:

800 SERIES	28-29

ABS & Stainless Steel Case, Liquid Filled:

900 SERIES	30-33

In keeping with and for purpose of product and/or manufacturing process improvements, NOSHOK, Inc. reserves the right to make design changes without prior notice.	3

T	A	B	L	E	O	F	C	O	N	T	E	N	T	S

DIFFERENTIAL PRESSURE GAUGES

Piston Type:

1000 SERIES	34-37

Diaphragm Type:

1100 SERIES	38-41

Dial Layouts:

1000 & 1100 SERIES	42-43

SANITARY PRESSURE GAUGES

Fractional:

10 SERIES	44-45

Heavy-Duty:

10 SERIES	46-47

DIAL INDICATING PRESSURE GAUGE OPTIONS & ACCESSORIES

Panel Mounting Flanges, Cases & Cover Rings, Lenses, Maximum Indicating Pointer, Set Pointers, Rubber Case Protectors, Recalibrators & Adjustable Pointers, Overpressure Protection, Ammonia Refrigeration Gauges, Liquid Filling Options, Special Connections, Reid Vapor Test Gauges, Metric Dials & Customized Special Dials, Certified

Calibration, Magnetic Spring Contact Switch	48-52

Options & Accessories by Gauge Series	53-54

Gauge Fill Options	55

Accuracy/Standard Dial Configurations	56-61

DIGITAL PRESSURE GAUGE

Digital Gauge:

1000 SERIES	62-63

INDUSTRIAL PRESSURE & LEVEL TRANSMITTERS &  TRANSDUCERS

Current Output:

100 SERIES	64-65

Voltage Output:

200 SERIES	66-67

Submersible Level:

612 SERIES	68-69

Cage-Protected Submersible Level:

613 SERIES	70-71

High Accuracy:

615/616 SERIES	72-73

Precision:

640 SERIES	74-75

Micro-sized:

660 SERIES	76-77

Electronic Indicating Pressure Transmitter/Switch:

800 SERIES	78-79

4

T	A	B	L	E	O	F	C	O	N	T	E	N	T	S

OEM TRANSMITTERS & TRANSDUCERS

Compact:

300 SERIES	80-81

High Volume:

650 SERIES	82-83

HAZARDOUS LOCATION PRESSURE & LEVEL TRANSMITTERS

Explosion-Proof:

621/622 SERIES	84-85

Non-Incendive:

623/624 SERIES	86-87

Intrinsically Safe:

625/626 SERIES	88-89

Intrinsically Safe Submersible Level:

627 SERIES	90-91

Intrinsically Safe Hammer Union:

628 SERIES	92-93

SANITARY PRESSURE TRANSMITTERS

ASME-BPE Sanitary Clamp:

11 SERIES	94-95

PRESSURE SWITCHES

Mechanical Miniature Low Pressure:

100 SERIES	96-97

Mechanical Compact SPDT:

200 SERIES	98-99

Mechanical Compact SPDT with Adjustable Hysteresis:

300 SERIES	100-101

Mechanical Heavy-Duty:

400 SERIES	102-103

Electronic Mag-Switch:

500 SERIES	104-105

Electronic Indicating Pressure Transmitter/Switch:

800 SERIES	106-107

ALL PRESSURE MEASUREMENT INSTRUMENTATION OPTIONS & ACCESSORIES

Piston-Type Snubbers, Sintered Snubbers, Pigtail Steam Syphons, Swivel Adaptors	108-111

Reference Information	112-123

Frequently Asked Questions	124-126

Canadian Registration Numbers	127

5

OPERATING SPECIFICATIONS

- Working Pressure Limitations

  - Dynamic Pressure

The working pressure should be limited to 60% of the dial range.

  - Static Pressure

The working pressure, where no sharp fluctuations occur, should be limited to 90% of the dial range

APPLICATIONS

- Hydraulics & pneumatics

- Medical

- Pumps & compressors

- Refrigeration controls

- Utilities

- Water management

100 SERIES

##### General purpose non-fillable dry gauge

- Vacuum and compound ranges through 0 psi to 15,000 psi

- 1-1/2", 2", 2-1/2" and 4" gauge sizes

- Standard impact-resistant ABS & Steel case

- Copper alloy and Brass wetted parts

|  | SERIES SPECIFICATIONS |  |
| --- | --- | --- |
| Pressure ranges | 100 Series (all) | Vacuum and compound ranges through 0 psi to 15,000 psi |
| Accuracy | 15-100, 15-110, 15-120, 20-100, 20-110, 20-120, 20-148, 25-100, 25-110, 25-120 | ±2.5% full scale |
|  | 40-100 | ±1.6% full scale |
| Temperature ranges* | 100 Series (all) | Media -4 °F to 140 °F (-20 °C to 60 °C) Ambient -40 °F to 140 °F (-40 °C to 60 °C) |
| Measuring element | 100 Series (all) | Copper alloy Bourdon tube |
| Connection | 15-100, 15-110, 15-120, 20-100, 20-110 | 1/8″ NPT, Brass |
|  | 20-148 | 1/8″ NPT/10-32 Female, Brass |
|  | 20-100, 20-110, 20-120, 25-100, 25-110, 25-120, 40-100 | 1/4″ NPT Brass SAE J1926-3:7/16-20 |
| Case | 15-100, 15-110, 20-100, 20-110, 20-148, 25-100, 40-100 | ABS (Acryl Nitril Butadien Styrol) |
|  | 15-120, 20-120, 25-120 | Black painted Steel with chrome triangular bezel and U-clamp |
| Bezel | 15-110, 20-110, 25-110 | Built-in bezel, molded as an integral part of the case for ease of panel mounting. |
|  | 15-120, 20-120, 25-120 | Chrome-plated Steel triangular bezel |
| Lens | 100 Series (all) | Acrylic |
| Pointer | 100 Series (all) | Molded plastic |
| Dial | 100 Series (all) | White background with black primary scale & red secondary scale. UV resistant. |
| Movement | 100 Series (all) | Brass & nylon, or all-Brass with highly polished bearing surfaces |

- For every 18 °F (10 °C) shift in temperature from which the gauge is calibrated, the user can experience up to ±0.4% additional error.

Dial Indicating Pressure Gauges

ABS & Steel Case, Dry

For details on accuracy/standard dial configuration

and dial layouts, see pages 56-61.

6

WARNING: This product can expose you to chemicals including Lead, which is known to the State of California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GAUGE SIZES | 15 | 1-1/2″ | 20 | 2″ | 25 | 2-1/2″ 40 | 4″ |
| CASE TYPES | 100 | ABS, bottom connection | 120 | Steel case panel mount |  |  |  |
|  | 110 | ABS, back connection | 148 | Square ABS, panel mount (2″ only) |  |  |  |
| PRESSURE | 30vac | -30 inHg vacuum to 0 psi | 30/300 | -30 inHg to 0 to 300 psi | 200 | 0 psi to 200 psi 2000 | 0 psi to 2,000 psi |
| RANGES | 30/15 | -30 inHg to 0 to 15 psi | 15 | 0 psi to 15 psi | 300 | 0 psi to 300 psi 3000 | 0 psi to 3,000 psi |
|  | 30/30 | -30 inHg to 0 to 30 psi | 30 | 0 psi to 30 psi | 400 | 0 psi to 400 psi 5000 | 0 psi to 5,000 psi |
|  | 30/60 | -30 inHg to 0 to 60 psi | 60 | 0 psi to 60 psi | 600 | 0 psi to 600 psi 6000 | 0 psi to 6,000 psi |
|  | 30/100 | -30 inHg to 0 to 100 psi | 100 | 0 psi to 100 psi | 1000 | 0 psi to 1,000 psi 10000 | 0 psi to 10,000 psi |
|  | 30/160 | -30 inHg to 0 to 160 psi | 160 | 0 psi to 160 psi | 1500 | 0 psi to 1,500 psi 15000 | 0 psi to 15,000 psi |
|  | 30/200 | -30 inHg to 0 to 200 psi |  |  |  |  |  |
|  |  |  |  | Other ranges available on request |  |  |  |
| SCALE OPTIONS*** | psi | psi single scale | psi/kPa | psi/kPa dual scale | psi/kg/cm2 | psi/kg/cm2 dual scale psi/bar | psi/bar dual scale |
| CONNECTION SIZES | 1/8 | 1/8″ NPT | SST | SAE J1926-3:7/16-20 Adjustable | 1/4 | 1/4″ NPT |  |
| OPTIONS | PMC SSB BLRF | Panel Mount Clamp Polished Stainless Steel Bezel Black Rear Flange | SSC CRC FAC | Stainless Steel Case Chrome Case Flat Sided ABS Case | LL GL SG | Polycarbonate Lens ST Glass Lens* CPO Safety Glass Lens* BP1 | Stainless Steel Tagging Brass Sintered Orifice 20 Micron Brass Press Fit Orifice 0.1 mm |
|  | BLFF | Black Front Flange – ABS Case | BCR | Black Cover Ring** | HL | Homalite Lens* BP3 | Brass Press Fit Orifice 0.3 mm |
|  | CFF | Chrome Front Flange – ABS Case | SSCR | Stainless Steel Cover Ring** | SP | Red Set Pointer** BP8 | Brass Press Fit Orifice 0.8 mm |
|  | SBFF | Black Front Flange – Steel Case | CCR | Chrome Cover Ring** | MIP | Maximum Indicating Pointer |  |
|  | SCFF | Chrome Front Flange – Steel Case | PCCR | Polished Chrome Cover Ring** | SDM | Silicone Dampened Movement |  |
|  | BSC | Black Steel Case | CAR | Chrome Adapter Ring* | LM | Laser Marking |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

NOTE: Refer to 100 Series options & accessories chart on page 50 for availability by part number.

* A Steel, Stainless or chrome case & cover ring must be additionally ordered when lenses other than acrylic are utilized on all 100 Series.

** Only 110 Series require a Steel, Stainless or chrome case & cover ring to be additionally ordered when utilizing a set pointer or cover ring.

Please consult factory when a set pointer is to be utilized on a 120 Series.

*** Other scales available on request

EXAMPLE	20 – 110 – 100 – psi – 1/4 – BSC

Gauge size	2"

Case type	ABS, back connection

Pressure range & scale option	psi to 100 psi

Connection size	1/4" NPT

Option	Black Steel Case

15-100 20-100 25-100

1.08"

(27.5 mm)

1.93"

(49 mm)

1.77"

(45 mm)

0.55"

(14 mm)

0.39"

(10 mm)

1.02"

(26 mm)

1.54"

(39 mm)

1.42"

(36 mm)

0.55"

(14 mm)

0.38"

(9.6 mm)

1.08"	 (27.5 mm)

2.11"

2.44"

(62 mm)

100 SERIES	INFORMATION

ORDERING

DIMENSIONS

(53.5 mm)

0.55"

(14 mm)

0.37"

(9.5 mm)	7

40-100 15-110

1.20" (30.5 mm)

3.94"

(100 mm)

3.29"

(83.5 mm)

0.87"

(22 mm)

0.45" (11.5 mm)

1.59"	 (40.5 mm)

0.18" (4.5 mm)

1.57"

(40 mm)

0.55"

(14 mm)

1.77"

(45 mm)

1.04" (26.5 mm)

20-110 20-148

1.67"

(42.5 mm)

0.18" (4.5 mm)

1.57" (40 mm)	 0.39" (10 mm)

0.16" (4 mm)

1.95"

(49.5 mm)

0.55"

(14 mm)

1.04" (26.5 mm)

2.13"

(54 mm)

1.77"

(45 mm)

0.55"

(14 mm)

1.06"

(27 mm)

1.90"

(48.5 mm)

25-110

1.67"

(42.5 mm)

0.22" (5.5 mm)

2.48"

(63 mm)

0.55"

(14 mm)

2.68"

(68 mm)

Dial Indicating Pressure Gauges

Dimensions

2.80" (71 mm)

1.59"	 (40.5 mm)

0.18"

(4.5 mm)

2.36" (60 mm)

1.67"	 (42.5 mm)

0.18"

(4.5 mm)

0.14"

(3.6 mm)

1.57"

(

40 mm)

1.95"

(49.5 mm)

0.55"

(14 mm)

0.14"

(3.6 mm)

0.55"

(14 mm)

8

120°

1.04" (26.5 mm)

120°

1.04" (26.5 mm)

20-110 Front Flange

15-110 Front Flange

2.40" (61 mm)

2.00" (51 mm)

1.40"  (35.5 mm)

25-110 Front Flange

1.67" (42.5 mm)

0.22"

(5.5 mm)

2.48"

(63 mm)

0.55"

(14 mm)

1.40" (35.5 mm)

3.35" (85 mm)

2.95" (75 mm)

0.14"

(3.6 mm)

120°

25-100 Rear Flange 40-100 Rear Flange

3.35" (85 mm)

2.95" (75 mm)

0.20"

(5 mm)

1.28" (32.5 mm)

5.20" (132 mm)

4.57" (116 mm)

0.20"

(5 mm)

1.40"

(35.5 mm)

0.14"

(3.6 mm)

120°

2.11"

(53.5 mm)

2.44"

(62 mm)

0.55"

(14 mm)

0.14"

(3.6 mm)

120°

3.94"

(100 mm)

3.29"

(83.5 mm)

0.55"

(14 mm)

15-120 Chrome Bezel With U-Clamp 20-120 Chrome Bezel With U-Clamp 25-120 Chrome Bezel With U-Clamp

1.84" (46.7 mm)

0.18"

1.98" (50.3 mm)

2.07" (52.6 mm)

0.19"	 		 	0.20"

(4.5 mm)

(4.9 mm)

(5 mm)

1.54"

(39 mm)

0.55"

(14 mm)

1.69"

(42.8 mm)

1.97"

(50 mm)

1.95"

(50 mm)

0.55"

(14 mm)

2.12"

(53.8 mm)

2.40"

(61 mm)

2.44"

(62 mm)

0.55"

(14 mm)

2.64"	3.58"

(67 mm) (91 mm)

1.12"	 (28.5 mm)

1.15"	 (29.3 mm)

1.25"	 (31.8 mm)

100 SERIES	DIMENSIONS

15-110 Panel Mount Clamp 20-110 Panel Mount Clamp 25-110 Panel Mount Clamp

1.77" (45 mm)

0.18"

(4.5 mm)

1.57"

(40 mm)

1.77"

(45 mm)

0.55"

(14 mm)

1.04" (26.5 mm)

1.85" (47 mm)

0.18"

(4.5 m

1.95"

(49.5 mm)

2.13"

(54 mm)

0.55"

(14 mm)

1.04" (26.5 mm)

1.87" (47.5 mm)

0.20"

(5 mm)

2.44"

(62 mm)

2.68"

(68 mm)

0.55"

(14 mm)

1.38"

(35 mm)

m)

##### 9

###### OPERATING SPECIFICATIONS

- Working Pressure Limitations

  - Dynamic Pressure

The working pressure should be limited to 60% of the dial range.

  - Static Pressure

The working pressure, where no sharp fluctuations occur, should be limited to 90% of the dial range

APPLICATIONS

  - Filter monitoring

  - Gas distribution

  - HVAC

  - Leak detection

  - Level indication

  - Medical

SERIES

200

Sensitive capsule-type, non-fillable dry gauge

- Vacuum ranges through 0 psi to 10 psi

- 2-1/2" and 4" gauge sizes

- Black painted Steel, Stainless Steel and impact-resistant ABS case

- Copper alloy and Brass wetted parts

|  | SERIES SPECIFICATIONS |  |
| --- | --- | --- |
| Pressure ranges | 200 Series (all) | Extreme low pressure vacuum ranges through 0 psi to 10 psi |
| Accuracy | 25-200, 25-210, 25-224 | ±1.6% full scale |
|  | 25-206, 25-216 | ±2.5% full scale |
|  | 40-200 | ±1.6% full scale; optional ±1% full scale |
| Temperature ranges* | 200 Series (all) | Media -4 °F to 176 °F (-20 °C to 80 °C) Ambient -4 °F to 140 °F (-20 °C to 60 °C) |
| Measuring element | 25-200, 25-210, 25-224, 40-200 | Copper alloy diaphragm capsule |
| Connection | 200 Series (all) | 1/4″ NPT, Brass |
| Case | 25-200, 25-210 | Black painted Steel |
|  | 25-206, 25-216, 25-224 | Black ABS (Acryl Nitril Butadien Styrol) with 25-224 includes zinc-plated Steel panel mount clamp |
|  | 40-200 | 304 Stainless Steel |
| Bezel | 40-200 | 304 Stainless Steel |
| Lens | 25-200, 25-206, 25-210, 25-216, 25-224 | Acrylic |
|  | 40-200 | Instrument glass |
| Pointer | 200 Series (all) | Black finished Aluminum |
| Dial | 200 Series (all) | Aluminum, white background with black scale. UV resistant. |
| Movement | 25-200, 25-210, 25-224, 40-200 | Brass and Nickel-silver with highly polished bearing surfaces |
|  | 25-206, 25-216 | Cu-Alloy |

- For every 18 °F (10 °C) shift in temperature from which the gauge is calibrated, the user can experience up to ±0.4% additional error.

Dial Indicating Pressure Gauges

Low Pressure Diaphragm

For details on accuracy/standard dial configuration

and dial layouts, see pages 56-61.

WARNING: This product can expose you to chemicals including Lead, which is known to the State of California to

10	cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| GAUGE SIZES | 25 | 2-1/2″ 40 4″ |  |  |  |  |
| CASE TYPES | 200 206 210 | Steel, bottom connection (304SS for 4″) ABS, bottom connection Steel, back connection | 216 224 234 | ABS, back connection ABS, panel mount Gas pressure test kit** |  |  |
| PRESSURE RANGES | 15 inH2O Vac 30 inH2O Vac 60 inH2O Vac 100 inH2O Vac 10 inH2O 15 inH2O 30 inH2O 60 inH2O | -15 inH2O to 0 inH2O 100 inH2O 0 inH2O to 100 inH2O -30 inH2O to 0 inH2O 160 inH2O 0 inH2O to 160 inH2O -60 inH2O to 0 inH2O 200 inH2O 0 inH2O to 200 inH2O -100 inH2O to 0 inH2O 10 oz/in2 0 oz/in2 to 10 oz/in2 0 inH2O to 10 inH2O 15 oz/in2 0 oz/in2 to 15 oz/in2 0 inH2O to 15 inH2O 30 oz/in2 0 oz/in2 to 30 oz/in2 0 inH2O to 30 inH2O 35 oz/in2 0 oz/in2 to 35 oz/in2 0 inH2O to 60 inH2O 60 oz/in2 0 oz/in2 to 60 oz/in2 | 100 oz/in2 160 oz/in2 20 oz/ in2/inH2O 32 oz/ in2/inH2O 3 psi 5 psi 10 psi 40 mbar | 0 oz/in2 to 100 oz/in2 0 oz/in2 to 160 oz/in2 0 oz/in2/inH2O to 20 oz/in2/inH2O 0 oz/in2/inH2O to 32 oz/in2/inH2O 0 psi to 3 psi 0 psi to 5 psi 0 psi to 10 psi 0 mbar to 40 mbar | 60 mbar 100 mbar 160 mbar 250 mbar 400 mbar 600 mbar | 0 mbar to 60 mbar 0 mbar to 100 mbar 0 mbar to 160 mbar 0 mbar to 250 mbar 0 mbar to 400 mbar 0 mbar to 600 mbar |
| CONNECTIONSIZE | 1/4 | 1/4″ NPT |  |  |  |  |
| OPTIONS | BLRF SSRF BLFF SSFF CFF SSC | Black Rear Flange GL Glass Lens* 304SS Rear Flange SG Safety Glass Lens* Black Front Flange*** PL Acrylic Lens 304SS Front Flange RL Recalibrator Lens Chrome Front Flange*** SP Red Set Pointer Stainless Steel Case MIP Maximum Indicating Pointer | OP SSBU BBU BCR SSCR | Over Pressure Protection Stainless Steel Bezel & U-Clamp Black Bezel & U-Clamp Black Cover Ring Stainless Steel Cover Ring | CCR LM ST BP3 BT3 | Chrome Cover Ring Laser Marking Stainless Steel Tagging Brass Press Fit Orifice 0.3 mm Brass Threaded Orifice 0.3 mm |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

NOTE: Refer to 200 Series Options & Accessories chart on page 51 for availability by part number.

- A Steel, Stainless or chrome cover ring must be additionally ordered when lenses other than acrylic are utilized on all 200 Series

** Only available in 2-1/2" size, 20 oz/35 inH2O

*** Not available on 25-200 model

EXAMPLE

Gauge size	.. 2-1/2"

Case type	Steel, bottom connection

Pressure range & scale option	0 inH20 to 30 inH20

Connection size	1/4" NPT

Option	Brass Press Fit Orifice 0.3 mm

25 – 200 – 30 – inH20 – 1/4 – BP3

200 SERIES	INFORMATION

ORDERING

DIMENSIONS

25-200 25-206 40-200 25-210

1.57" (40 mm)

2.48"

(63 mm

2.05"

2 mm)

0.55"

(14 mm)

0.37"

(9.5 mm)

1.36" (34.5 mm)

1.16"	 (29.5 mm)

0.94"

(24 mm)

2.44"

(62 mm)

1.89"

(48 mm)

0.55"

(14 mm)

1.00" (25.5 mm)

2.19" (55.5 mm)

2.48"

(63 mm)

0.55"

(14 mm)

1.44"	 (36.5 mm)

1.94" (49.3 mm)

3.98"

(101 mm)

3.35"

(85 mm)

0.87"

(22 mm)

0.61"

(15.5 mm)

)

(5

##### 11

25-216 25-210 Front Flange

3.35" (85 mm)

2.95" (75 mm)

0.14" (3.6 mm)

120°

2.03" (51.5 mm)

0.16"

(4 mm)

2.48"

(63 mm)

0.55"

(14 mm)

1.44"	 (36.5 mm)

2.03" (51.5 mm)

2.44"

(62 mm)

0.55"

(14 mm)

0.94"

(24 mm)

25-200 Rear Flange

3.35" (85 mm)

2.95" (75 mm)

1.77" (45 mm)

0.20"

(5 mm)

2.48"

(63 mm)

0.14" (3.6 mm)

2.05"

(52 mm)

Dial Indicating Pressure Gauges

Dimensions

0.55"

(14 mm)

120°

40-200 Rear Flange

0.12"

(3 mm)

1.95"	 (49.6 mm)

3.98"

(101 mm)

3.35"

(85 mm)

0.87"

(22 mm)

5.20" (132 mm)

4.57" (116 mm)

0.14"

(3.6 mm)

120°

##### 12

200 SERIES	DIMENSIONS

25-210 Triangular  Bezel w/U-Clamp

2.37" (60.2 mm)

0.16"

(4 mm)

2.49"

(63.2 mm)

2.70"

(68.5 mm)

0.55"

(14 mm)

1.55" (39.4 mm)

25-224 with Panel Mount Clamp

2.03" (51.6 mm)

0.28"

(7 mm)

2.59"

(65.9 mm)

2.84"

(72.2 mm)

0.55"

(14 mm)

1.58" (40.2 mm)

25-234

7.50"

(190.5 mm)

5.75" (146.1 mm)

2.06" (52.3 mm)

13

300

SERIES

  - High quality, heavy-duty liquid filled gauge

  - Vacuum and compound ranges through 0 psi to 15,000 psi

  - 2-1/2" and 4" gauge sizes

  - Die cast Brass case with natural Brass finish

  - Copper alloy or 316 Stainless Steel and Brass wetted parts

OPERATING SPECIFICATIONS

- Working Pressure Limitations

  - Dynamic Pressure

The working pressure should be limited to 60% of the dial range.

  - Static Pressure

The working pressure, where no sharp fluctuations occur, should be limited to 90% of the dial range.

APPLICATIONS

- Automotive

- Construction

- Hydraulics & pneumatics

- Mining

- Stamping & forming presses

- Transportation

|  | SERIES SPECIFICATIONS |  |
| --- | --- | --- |
| Pressure ranges | 300 Series (all) | Vacuum and compound ranges through 0 psi to 15,000 psi |
| Accuracy | 25-300, 25-310 | ±1.6% full scale |
|  | 40-300, 40-310 | ± 1% full scale |
| Temperature ranges* | 300 Series (all) | Media -4 °F to 140 °F (-20 °C to 60 °C) Ambient 0 °F to 160 °F (-18 °C to 71 °C) Optional temperature ratings available from -40 °F to 212 °F (-40 °C to 100 °C) |
| Measuring element | 25-300, 25-310 (≤ 600 psi) | Copper alloy “C” tube |
|  | 25-300, 25-310 (800 psi to 6,000 psi) | Copper alloy coiled safety tube |
|  | 25-300, 25-310 (7,500 psi to 15,000 psi) | 316 Stainless Steel coiled safety tube |
|  | 40-300, 40-310 (≤ 1,000 psi) | Copper alloy “C” tube |
|  | 40-300, 40-310 (15,000 psi) | 316 Stainless Steel coiled safety tube |
| Connection | 25-300, 25-310 | 1/4″ NPT die-cast Brass with the case. 7/16″ – 20 SAE adjustable type straight thread with FKM O-ring is also available as a stock option on many ranges (-4 SAE). |
|  | 40-300, 40-310 | 1/4″ NPT die-cast Brass with the case. 1/2″ NPT is available on certain 40-300 ranges as a stock option, and on all other 40-300 and 40-310’s as a non-stock option. |
| Case | 300 Series (all) | Die cast Brass (natural Brass finish) with safety relief plug |
| Cover ring | 300 Series (all) | Polished Brass |
| Lens | 300 Series (all) | Acrylic with o-ring seal |
| Pointer | 300 Series (all) | Balanced Aluminum, black finish |
| Dial | 300 Series (all) | Aluminum, white background with black scale. UV resistant. |
| Movement | 300 Series (all) | Brass and Nickel-silver with highly polished bearing surfaces |
| Fill liquid** | 300 Series (all) | Glycerin |

For every 18 °F (10 °C) shift in temperature from which the gauge is calibrated, the user can experience up to ±0.4% additional error.

**See page 51 for gauge fill options.

Dial Indicating Pressure Gauges

Brass Case, Liquid Filled

For details on accuracy/standard dial configuration

and dial layouts, see pages 56-61.

WARNING: This product can expose you to chemicals including Lead, which is known to the State of California to

14	cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GAUGE SIZES | 25 | 2-1/2″ | 40 | 4″ |  |  |  |  |
| CASE TYPES | 300 | Brass, bottom connection | 310 | Brass, back connection |  |  |  |  |
| PRESSURE RANGES | 30vac 30/15 30/30 30/60 30/100 30/160 30/200 | -30 inHg to 0 psi -30 inHg to 0 to 15 psi -30 inHg to 0 to 30 psi -30 inHg to 0 to 60 psi -30 inHg to 0 to 100 psi -30 inHg to 0 to 160 psi -30 inHg to 0 to 200 psi | 30/300 15 30 60 100 160 200 | -30 inHg to 0 to 300 psi 0 psi to 15 psi 0 psi to 30 psi 0 psi to 60 psi 0 psi to 100 psi 0 psi to 160 psi 0 psi to 200 psi | 300 400 600 800 1000 1500 2000 | 0 psi to 300 psi 0 psi to 400 psi 0 psi to 600 psi 0 psi to 800 psi 0 psi to 1,000 psi 0 psi to 1,500 psi 0 psi to 2,000 psi | 3000 5000 6000 7500 10000 15000 | 0 psi to 3,000 psi 0 psi to 5,000 psi 0 psi to 6,000 psi 0 psi to 7,500 psi 0 psi to 10,000 psi 0 psi to 15,000 psi |
| SCALE OPTIONS | psi | psi single scale | psi/kPa | psi/kPa dual scale | psi/kg/cm2 | psi/kg/cm2 dual scale | psi/bar | psi/bar dual scale |
| CONNECTION SIZES 1/4 1/4″ NPT 1/2 1/2″ NPT SST SAE J1926-3:7/16-20 Adjustable |  |  |  |  |  |  |  |  |
| OPTIONS | CFF CFFN BFF BLFF SSRF | Chrome Front Flange Chrome Front Flange w/o holes Brass Front Flange Black Front Flange 304SS Rear Flange | RF CCR CBU MIP LL | Rear Flange Chrome Cover Ring Chrome Bezel & U-Clamp Maximum Indicating Pointer Polycarbonate Lens | GLO SGO AR LM | Glass Lens Overlay Safety Glass Overlay Adapter Ring Laser Marking | ST BT3 BT4 BT8 | Stainless Steel Tagging Brass Threaded Orifice 0.3 mm Brass Threaded Orifice 0.4 mm Brass Threaded Orifice 0.8 mm |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

NOTE: Refer to 300 Series Options & Accessories chart on page 51 for availability by part number.

EXAMPLE	40 – 300 – 3000 – psi – 1/4 – BT3

Gauge size	4"

Case type	Brass, bottom connection

Pressure range & scale option	psi to 3,000 psi

Connection size	1/4" NPT

Option	Brass Press Fit Orifice 0.3 mm

25-300 40-300 25-310

1.34"

(34 mm)

2.48"

(63 mm)

2.13"

(54 mm)

0.55"

(14 mm)

0.43"

(11 mm)

1.77"

2.36" (60 mm)

2.48"

(63 mm)

0.55"

(14 mm)

1.34"

(34 mm)

(45 mm)

3.94"

(100 mm)

3.46"

(88 mm)

0.87"

(22 mm)

0.53"

(13.5 mm)

300 SERIES	INFORMATION

ORDERING

DIMENSIONS

15

40-310 25-300 Front Flange

3.46" (88 mm)

3.35" (85 mm)

1.38"

(35 mm)

0.08"

(2 mm)

2.48"

(63 mm)

2.09"

(53 mm)

0.55"

(14 mm)

0.43"

(11 mm)

2.95" (75 mm)

1.18"

(30 mm)

3.94"

(100 mm)

0.14"

(3.6 mm)

0.87"

(22 mm)

1.77" (45 mm)

120°

40-300 Front Flange 25-310 Front Flange

5.20" (132 mm)

4.53" (115 mm)

"

120°

1.79"

(45.5 mm)

0.14"

(3.5 mm)

3.35" (85 mm)

2.48" (63 mm)

0.08"

(2 mm

2.48"

(63 mm)

0.55"

(14 mm)

1.46"

(37 mm)

2.95" (75 mm)

)

0.20

(5 mm)

3.98"

(101 mm)

3.15"

(80 mm)

0.14"

(3.6 mm)

0.87"

(22 mm)

120°

40-310 Front Flange 25-300 Rear Flange

0.08"

(2 mm)

1.46"

(37 mm)

2.48"

(63 mm)

2.09"

(53 mm)

0.55"

(14 mm)

3.35" (85 mm)

2.95" (75 mm)

5.20" (132 mm)

2.78"	 (70.5 mm)

0.14"

(3.5 m

3.94"

(100 mm)

1.93"

(49 mm)

4.53" (115 mm)

m)

0.20"

(5 mm)

0.14"

(3.6 mm)

120°

0.87"

(22 mm)

Dial Indicating Pressure Gauges

Dimensions

120°

##### 16

40-300 Rear Flange 25-310 Rear Flange

5.20" (132 mm)

4.57" (116 mm)

0.20"

5 mm)

0.08"

(2 mm)

1.85"

0.20"

(5 mm)

1.54"

(39 mm)

2.36" (60 mm)

3.35" (85 mm)

2.95" (75 mm)

(47 mm)

3.94"

(100 mm)

(	3.46"

(88 mm)

0.14"

(3.5 mm)	0.55"

(14 mm)

2.48"

(63 mm)

300 SERIES	DIMENSIONS

0.87"

(22 mm)

120°	120°

###### 40-310 Rear Flange

1.85" (47 mm)

0.08"

(2 mm)

3.94"

(100 mm)

1.18"

(30 mm)

0.87"

(22 mm)

3.46" (88 mm)

5.20" (132 mm)

4.57" (116 mm)

0.20"

(5 mm)

120°

25-310 Chrome Triangular Bezel with U-Clamp 40-310 Chrome Triangular Bezel with U-Clamp

2.36" (60 mm)

0.16"

(4 mm)

2.48"

(63 mm)

2.68"

(68 mm)

0.55"

(14 mm)

1.26"

(32 mm)

3.46" (88 mm)

0.16"

(4 mm)

3.94"

(100 mm)

1.18"

(30 mm)

4.21"

(107 mm)

0.87"

(

22 mm)

1.93"

(49 mm)

##### 17

Dial Indicating Pressure Gauges

All Stainless Steel, Dry & Liquid Filled

###### OPERATING SPECIFICATIONS

- Working Pressure Limitations

  - Dynamic Pressure

The working pressure should be limited to 60% of the dial range.

  - Static Pressure

The working pressure, where no sharp fluctuations occur, should be limited to 90% of the dial range

APPLICATIONS

- Chemical processing

- Oil field & offshore

- Paper mills

- Agriculture plants

- Marine

- Water & wastewater

- For every 18 °F (10 °C) shift in temperature from which the gauge is calibrated, the user can experience up to ±0.4% additional error.

** See page 51 for gauge fill options.

For details on accuracy/standard dial configuration

and dial layouts, see pages 56-61.

18

SERIES

400/500

Corrosion-resistant fillable dry or liquid-filled gauge

- Vacuum and compound ranges through 0 psi to 20,000 psi

- 1-1/2", 2-1/2", 4 and 6" gauge sizes

- Stainless Steel case

- 316 Stainless Steel wetted parts

- ECE-R110 Certification for CNG/LNG Pressure Gauge Component

(Part number 25-410-300-psi/bar only)

|  | SERIES SPECIFICATIONS |  |
| --- | --- | --- |
| Pressure ranges | 400/500 Series (all) | Vacuum and compound ranges through 0 psi to 20,000 psi |
| Accuracy | 15-401, 15-411 | ±2.5% full scale |
|  | 25-400, 25-410, 25-500, 25-510 | ±1.6% full scale |
|  | 40-400, 40-410, 40-500, 40-510, 60-400, 60-410, 60-500, 60-510 | ±1% full scale |
| Temperature ranges* | 15-401, 15-411 | Media -40 °F to 212 °F (-40 °C to 100 °C) Ambient -40 °F to 140 °F (-40 °C to 60 °C) |
|  | 25-400, 25-410, 40-400, 40-410, 60-400, 60-410 | Media -40 °F to 392 °F (-40 °C to 200 °C) Ambient -40 °F to 140 °F (-40 °C to 60 °C) |
|  | 500 Series (all) | Media -4 °F to 212 °F (-20 °C to 100 °C) Glycerin fill -40 °F to 212 °F (-40 °C to 100 °C) Special fill Ambient -4 °F to 140 °F (-20 °C to 60 °C) Glycerin fill -40 °F to 140 °F (-40 °C to 60 °C) Special fill |
| Measuring element | 15-401, 15-411, 25-400, 25-410, 25-500, 25-510, 40-400, 40-410, 40-500, 40-510, 60-400, 60-410, 60-500, 60-510 (up to 600 psi) | 316 Stainless Steel C-Type Bourdon tube |
|  | 25-400, 25-410, 25-500, 25-510, 40-400, 40- 410, 40-500, 40-510, 60-400, 60-410, 60-500, 60-510 (greater than 600 psi) | Coiled safety tube |
| Connection | 15-401, 15-411 | 1/8″ NPT, 316 Stainless Steel |
|  | 25-400, 25-410, 25-500, 25-510 | 1/4″ NPT, 316 Stainless Steel |
|  | 40-400, 40-410, 40-500, 40-510, 60-400, 60-410, 60-500, 60-510 | 1/2″ NPT, 316 Stainless Steel. 9/16″ – 18 high pres- sure connections are standard on 0 - 30,000 psi and higher |
| Case | 15-401, 15-411, 40-400, 40-410, 60-400, 60-410, 60-500, 60-510 | 304 Stainless Steel (Optional 316 Stainless Steel) with safety relief plug |
|  | 25-400, 25-410, 25-500, 25-510, 40-500, 40-510 | Polished 304 Stainless Steel with safety relief plug |
| Cover ring | 15-401, 15-411, 25-400, 25-410, 25-500, 25-510, 40-400, 40-410, 40-500, 40-510 | Polished 304 Stainless Steel |
|  | 60-400, 60-410, 60-500, 60-510 | Polished 304 Stainless Steel bayonet ring |
| Lens | 15-401, 15-411, 40-400, 40-410, 40-500, 40-510 | Instrument glass |
|  | 25-400, 25-410, 25-500, 25-510 | Trogamide |
|  | 60-400, 60-410, 60-500, 60-510 | Laminated safety glass |
| Pointer | 115-401, 15-411 | Black finished Aluminum |
|  | 25-400, 25-410, 25-500, 25-510, 40-400, 40-410, 40-500, 40-510 | Balanced Aluminum, black finish |
|  | 60-400, 60-410, 60-500, 60.510 | Balanced micro-adjustable Aluminum, black finish |
| Dial | 15-401, 15-411 | Aluminum, white background with black scale. Single scale psi. UV resistant |
|  | 25-400, 25-410, 25-500, 25-510, 40-400, 40-410, 40-500, 40-510, 60-400, 60-410, 60-500, 60-510 | Aluminum, white background with black scale. UV resistant. |
| Movement | 15-401, 15-411, 25-400, 25-410, 25-500, 25-510 | Stainless Steel with highly polished bearing surfaces |
|  | 40-400, 40-410, 40-500, 40-510 | All Stainless Steel with internal zero stop and highly polished bearing surfaces |
|  | 60-400, 60-410, 60-500, 60-510 | Stainless Steel with highly polished bearing surfaces An internal zero stop is standard |
| Fill liquid** | 25-500, 25-510, 40-500, 40-510, 60-500, 60-510 | Glycerin |

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| GAUGE SIZE | 15 | 1-1/2″ | 25 | 2-1/2″ 40 4″ * |  | 60 6″ * |
| CASE TYPES | 400 401 | All SS, dry/fillable, bottom connection All SS, dry, bottom connection | 410 411 | All SS, dry/fillable, back connection All SS, dry, back connection | 502 | SS case, solid front, liquid filled, bottom connection |
|  | 402 | SS case, solid front, dry, bottom connection | 500 | SS case, liquid filled, bottom connection | 510 | SS case, liquid filled, back connection |
| PRESSURE | 30vac | -30 inHg to 0 psi *** | 30 | 0 psi to 30 psi | 1000 | 0 psi to 1,000 psi |
| RANGES | 30/15 | -30 inHg to 0 psi to 15 psi *** | 60 | 0 psi to 60 psi | 1500 | 0 psi to 1,500 psi |
|  | 30/30 | -30 inHg to 0 psi to 30 psi *** | 100 | 0 psi to 100 psi | 2000 | 0 psi to 2,000 psi |
|  | 30/60 | -30 inHg to 0 psi to 60 psi *** | 160 | 0 psi to 160 psi | 3000 | 0 psi to 3,000 psi |
|  | 30/100 | -30 inHg to 0 psi to 100 psi *** | 200 | 0 psi to 200 psi | 5000 | 0 psi to 5,000 psi |
|  | 30/160 | -30 inHg to 0 psi to 160 psi *** | 300 | 0 psi to 300 psi | 6000 | 0 psi to 6,000 psi |
|  | 30/200 | -30 inHg to 0 psi to 200 psi *** | 400 | 0 psi to 400 psi | 10000 | 0 psi to 10,000 psi |
|  | 30/300 | -30 inHg to 0 psi to 300 psi *** | 600 | 0 psi to 600 psi | 15000 | 0 psi to 15,000 psi |
|  | 15 | 0 psi to 15 psi | 800 | 0 psi to 800 psi | 20000 | 0 psi to 20,000 psi ** |
| SCALE OPTIONS | psi psi/kPa | psi single scale psi/kPa dual scale | psi/kg/cm2 psi/bar | psi/kg/cm2 dual scale psi/bar dual scale |  |  |
| CONNECTION SIZES | 1/8 | 1/8″ NPT | 1/2 | 1/2″ NPT | SST | SAE J1926-3:7/16-20 Adjustable |
|  | 1/4 | 1/4″ NPT | 9/16-18 | 9/16″-18 UNF 2B high pressure cone |  |  |
| OPTIONS | SSFF SSRF SSBU SPMC | 304SS Front Flange 304SS Rear Flange Stainless Steel Bezel & U-Clamp 304SS Panel Mount Clamp | SSFR AP SG MIP | 304SS Flange Ring Adjustable Pointer Safety Glass Lens Maximum Indicating Pointer | LM ST ST5 ST8 | Laser Marking Stainless Steel Tagging Stainless Steel Threaded Orifice 0.5 mm Stainless Steel Threaded Orifice 0.8 mm |
|  | PMC | Steel Panel Mount Clamp | SP | Red Set Pointer |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

NOTE: Refer to 400/500 Series options & Accessories chart on page 52 for availability by part number.

* On 40-400, 40-410, 40-500, 40-510, 60-400, 60-410, 60-500, and 60-510 models with 20,000 psi, the accuracy is ±1.5% or 1.6%

** 4" model only available with solid front case types

*** Ammonia gauges are available in these ranges. To order, add " – AMMONIA" at the end of the part number.

EXAMPLE	40 – 500 – 600 – psi – 1/2 – MIP

Gauge size	4"

Case type	SS case, liquid filled, bottom connection

Pressure range & scale option	psi to 600 psi

Connection size	1/2" NPT

Option	Maximum Indicating Pointer

| 15-401 | 25-400/500 | 40-400/500 |  |
| --- | --- | --- | --- |
|  |  | 2.13" |  |
|  | 1.26" | (54 mm) |  |
| 0.98" | (32 mm) |  |  |

2.68"

(68 mm)

2.13"

(54 mm)

0.55"

(14 mm)

0.51"

(13 mm)

(25 mm)

1.57"

(40 mm)

3.98"

(101 mm)

1.54"

(39 mm)

0.55"

3.43"

(87 mm)

0.87"

(14 mm)

0.35"

(9 mm)

(22 mm)

0.70" (17.7 mm)

400/500 SERIES	INFORMATION

ORDERING

DIMENSIONS

19

60-400/500 15-411 25-410/510 40-410/510

*1.95"

* ≥ 1,500 psi increase by 0.67" (17 mm)

(49.5 mm)

1.61" (40.9 mm)		 1.97" (50 mm )	 	0.20"

(5 mm)

3.37" (85.5 mm)

4.65"

(118 mm)

6.34"

(161 mm)

0.55"

1.57"

(40 mm)

2.44"

(62 mm)

0.55"

2.68"

(68 mm)

1.18"

(30 mm)

3.98"

(101 mm)

(14 mm)

0.87"

(22 mm)

0.61" (15.5 mm)

1.06" (27 mm)

(14 mm)

1.26"

(32 mm)

0.87"

(22 mm)	 2.13"

(54 mm)

60-410/510 40-400/500 Front Flange 60-400/500 Front Flange

3.35" (85 mm)

2.95" (75 mm)

5.20" (132 mm)

4.57" (116 mm)

7.72" (196 mm)

7.01" (178 mm)

*2.95"

(75 mm)

0.31"

(8 mm)

5.20" (132 mm)

4.57" (116 mm)

0.08"

(2 mm)

2.20"

*3.27"

(83 mm)

5.20" (132 mm)

4.57" (116 mm)

1.81"

(46 mm)

0.24"

(6 mm)

7.72" (196 mm)

7.01" (178 mm)

*1.63" (41.5 mm)

0.31"

(8 mm)

0.19"

(	)

4.8 mm

(13.97"

01 mm)

6.34"

(161 mm)

1.97"

(50 mm)

6.34"

(161 mm)

0.20"

(5 mm)

0.87"

(22 mm)

3.43"

(87 mm)

*1.95" (49.5 mm)

* ≥ 1,500 psi increase

by 0.67" (17 mm)

120°

0.87"

(22 mm)

0.70"

(17.7 mm)

4.65"

(118 mm)

120°

0.61"

(15.5 mm)

0.87"

(22 mm)

1.97" (50 mm)

0.20"

(5 mm)

3.13" (79.5 mm)

0.24"

(6 mm)

0.14" (3.6 mm)

2.68"

(68 mm)

3.97"

(101 mm)

0.55"

(14 mm)

0.19" (4.8 mm)

1.18"

(30 mm)

1.26"

(32 mm)

0.87"

(22 mm)

120°

2.13"

(54 mm)

40-400/500 Rear Flange

60-410/510 Front Flange

40-410/510 Front Flange

25-410/510 Front Flange

(56 mm)

0.20"

(5 mm)

1.97"

(50 mm)

6.34"

(161 mm)

0.20"

(5 mm)

3.43"

3.97"

(101 mm)

0.87"

(22 mm)

(87 mm)

0.87"

Dial Indicating Pressure Gauges

Dimensions

20	120°

1.95"

(49.5* mm)

- ≥ 1,500 psi increase

by 0.67" (17 mm)

120°

0.70" (17.7 mm)

(22 mm)

60-400/500 Rear Flange 40-410/510 Rear Flange

7.72" (196 mm)

7.01" (178 mm)

0.11"

*1.91" (48.5 mm)

0.11"

2.07" (52.5 mm)

(3 mm)

1.18"

(30 mm)

3.98"

(101 mm)

0.87"

(22 mm)

3.27"

(83 mm)

5.20" (132 mm)

(3 mm)

4.57" (116 mm)

0.23"

(5.8 mm)

120°

4.65"

(118 mm)

0.61"

(15.5 mm)

6.34"

(161 mm)

0.87"

(22 mm)

0.20"

(5 mm)

120°

60-410/510 Rear Flange 25-410/510 Flange Ring

1.26"

(32 mm)

0.55"

(14 mm)

2.44"

(62 mm)

2.68"

(68 mm)

1.89"

(48 mm)

0.20"

(5 mm)

7.72" (196 mm)

7.01" (178 mm)

*1.95" (49.5 mm)

3.35" (85mm)

0.11"

(3 mm)

0.23"

(5.8 mm)

120°

1.97"

(50 mm)

0.87"

(22 mm)

6.34"

(161 mm)

*3.27"

(83 mm)

120°

25-410/510 Panel Mount Clamp 40-410/510 SS Narrow Bezel w/U-Clamp 60-410/510 SS Narrow Bezel w/U-Clamp

3.21" (81.5 mm)

(4 mm

0.16"

3.98"

(101 mm)

1.18"

(30 mm)

4.21"

(107 mm)

0.87"

(22 mm)

2.13"

(54 mm)

2.17" (55 mm)		0.20"

(5 mm)

2.44"

(62 mm)

2.68"

(68 mm)

0.55"

(14 mm)

1.26"

(32 mm)

)

6.34"

(161 mm)

1.97"

(50 mm)

3.07" (78 mm)

0.20"

(5 mm)

6.85"

(174 mm)

0.87"

(22 mm)

*1.95" (49.5 mm)

400/500 SERIES	DIMENSIONS

* Dimension will be 0.67" (17 mm) for pressure ranges above 1,500 psi.

21

OPERATING SPECIFICATIONS

- Working Pressure Limitations

  - Dynamic Pressure

The working pressure should be limited to 65% of the dial range.

  - Static Pressure

The working pressure, where no sharp fluctuations occur, should be limited to 75% of the dial range

APPLICATIONS

  - Pumps & compressors

  - High pressure processing

  - Test equipment & systems

  - Water jet cutting

For details on accuracy/standard dial configuration

and dial layouts, see pages 56-61.

SERIES

402/502

Corrosion-resistant dry or liquid-filled gauge for high pressure applications

- Ranges from 0 psi to 30,000 psi through 0 psi to 85,000 psi

- 4" and 6" gauge sizes

- Solid front design with a blow out back in accordance to EN 837, S3 Safety Pattern

- Stainless Steel case

- NiFe alloy/316L Stainless Steel wetted parts

- DIN 16001 compliant

SERIES	SPECIFICATIONS

| Pressure ranges | 402, 412 & 500 Series | 0 psi to 30,000 psi through 0 psi to 85,000 psi |
| --- | --- | --- |
| Accuracy | ≤40,000 psi | ±1.6% full scale (optional 1% increased accuracy) |
|  | ≥50,000 psi | ±1% full scale (85,000 psi is ±1.6% accuracy) |
| Temperature ranges* | 402 & 412 Series | Media -40 °F to 392 °F (-40 °C to 200 °C) Ambient -40 °F to 140 °F (-40 °C to 60 °C) |
|  | 502 Series | Media -4 °F to 212 °F (-20 °C to 100 °C) Glycerin fill Ambient -4 °F to 140 °F (-20 °C to 60 °C) Glycerin fill |
| Measuring element | 402/502 Series (all) | NiFe alloy |
| Connection | 402/502 Series (all) | 316L Stainless Steel |
| Case | 402/502 Series (all) | Stainless Steel, solid front with blowout back |
| Cover ring | 402/502 Series (all) | Stainless Steel bayonet ring |
| Lens | 402/502 Series (all) | Laminated safety glass |
| Pointer | 402/502 Series (all) | Black finished Aluminum |
| Dial | 402/502 Series (all) | Aluminum, white background with black scale. UV resistant. |
| Movement | 402/502 Series (all) | Stainless Steel with highly polished bearing surfaces |
| Fill liquids | 502 Series (Bottom connected only) | Glycerin |

- For every 68 °F (20 °C) shift in temperature from which the gauge is calibrated, the user can experience up to ±0.4% additional error.

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

Dial Indicating Pressure Gauges

All Stainless Steel, Dry & Liquid Filled, Extreme High Pressure

##### 22

| ORDERING INFORMATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| GAUGE SIZE | 40 | 4″ | 60 | 6″ * |  |  |
| CASE TYPES | 402 | Dry, bottom connection | 412 | Dry, lower back connection | 502 | Liquid filled, bottom connection |
| PRESSURE RANGES | 30000 40000 | 0 psi to 30,000 psi 0 psi to 40,000 psi | 50000 60000 | 0 psi to 50,000 psi 0 psi to 60,000 psi | 75000 85000 | 0 psi to 75,000 psi 0 psi to 85,000 psi ** |
| SCALE OPTIONS | psi psi/kPa | psi single scale psi/kPa dual scale | psi/kg/cm2 psi/bar | psi/kg/cm2 dual scale psi/bar dual scale |  |  |
| CONNECTION SIZES *** | 9/16-18 | 9/16″-18 UNF 2B high pressure cone - Female | 9/16-HPM | 9/16″-18 UNF 2A left hand thread - Male |  |  |
| OPTIONS | BRSP LM MIP | Bayonet Ring Adjustable Set Pointer Laser Marking Maximum Indicating Pointer | SL SP SSFF | Silicone Fill Red Set Pointer 304SS Front Flange | ST IA | Stainless Steel Tagging Increased Accuracy |

*	Bottom connection only.

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

402/502 SERIES	INFORMATION

ORDERING

DIMENSIONS

** Only available on 60-402 and 60-502 models, with ±1.6% accuracy.

*** Additional process connection sizes available, consult factory.

EXAMPLE	40 – 402 – 30000 – psi – 9/16-18 – BRSP

Gauge size	4"

Case type	Dry, bottom connection

Pressure range & scale option	psi to 30,000 psi

Connection size	9/16″-18 UNF 2B high pressure cone

Option	Bayonet Ring Adjustable Set Pointer

9/16″-18 UNF 2B High Pressure Cone Connection

Female	Male

23

40-402/502 40-412

2.32"

(59 mm)

0.67"

(17 mm)

3.90"

(99 mm)

3.98"

(101 mm)

3.43"

(87 mm)

0.87" sq

(22 mm)

0.98"

(25 mm)

2.34"

(59.5 mm)

0.67"

(17 mm)

3.90"

(99 mm)

1.18"

(30 mm)

3.98"

(101 mm)

0.87" sq

(22 mm)

3.66"

(93 mm)

60-402/502 40-402/502 Front Flange

2.56"

(65 mm)

0.69"

2.32"

(59 mm)

0.24"

(6 mm)

3.90"

(99 mm)

5.20"

(132 mm)

3.98"

(101 mm)

3.43"

(87 mm)

0.87" sq (22 mm)

0.98"

(25 mm)

(17.5 mm)

6.26"

(159 mm)

6.34"

(161 mm)

4.65"

(118 mm)

1.06"

(27 mm)

0.87" sq

(22 mm)

Dial Indicating Pressure Gauges

Dimensions

24

40-412  Front Flange

2.34"

(59.5 mm)

0.24"

(6 mm)

3.90"

(

99 mm)

3.98"

(101 mm)

5.20"

(132 mm)

1.18"

(30 mm)

0.87" sq

(22 mm)

3.43"

(87 mm)

60-402/502  Front Flange

2.56"

(65 mm)

0.31"

(8 mm)

6.26"

(159 mm)

6.34"

(161 mm)

7.72"

(196 mm)

4.65"

(118 mm)

1.06"

(27 mm)

  - " sq

(22 mm)

402/502 SERIES	DIMENSIONS

25

600/700

SERIES

    - Turret style dry or liquid-filled gauge

    - Vacuum and compound ranges through 0 psi to 15,000 psi

    - 4-1/2" gauge sizes

    - Black phenolic safety case with solid front and blow-out back PBT

    - Phosphor bronze, 316 Stainless Steel and Brass wetted parts

|  | SERIES SPECIFICATIONS |  |
| --- | --- | --- |
| Pressure ranges | 600/700 Series (all) | Vacuum and compound ranges through 0 psi to 15,000 psi |
| Accuracy | 600/700 Series (all) | ±0.5% full scale |
| Temperature ranges* | 45-640 | Media -4 °F to 150 °F (-20 °C to 65 °C) Ambient -40 °F to 150 °F (-40 °C to 65 °C) |
|  | 45-740 | Media -40 °F to 212 °F (-40 °C to 100 °C) 500 °F (260 °C) Maximum for short term/intermittent Ambient -40 °F to 150 °F (-40 °C to 65 °C) |
|  | 45-660 | Media -4 °F to 150 °F (-20 °C to 65 °C) Glycerin fill -40 °F to 150 °F (-40 °C to 65 °C) Special fill Ambient -4 °F to 150 °F (-20 °C to 65 °C) Glycerin fill -40 °F to 150 °F (-40 °C to 65 °C) Special fill |
|  | 45-760 | Media -4 °F to 212 °F (-20 °C to 100 °C) Glycerin fill -40 °F to 212 °F (-40 °C to 100 °C) Special fill 250 °F (130 °C) Maximum for short term/intermittent Ambient -4 °F to 150 °F (-20 °C to 65 °C) Glycerin fill -40 °F to 150 °F (-40 °C to 65 °C) Special fill |
| Case | 600/700 Series (all) | Turret style black phenolic case. Solid front, safety case with blow-out back PBT. |
| Bayonet ring | 600/700 Series (all) | Threaded black PBT |
| Lens | 600/700 Series (all) | Acrylic |
| Measuring Element | 45-640, 45-660 (≤ 600 psi) | Copper alloy C-Type Bourdon tube |
|  | 45-740, 45-760 (≤ 600 psi) | 316 Stainless Steel C-Type Bourdon tube |
|  | 600/700 Series (all) (>600 psi) | 316 Stainless Steel coiled safety Bourdon tube |
| Connection | 45-640, 45-660 | 1/4″ NPT, Brass |
|  | 45-740, 45-760 | 1/4″ NPT or 1/2″ NPT, 316 Stainless Steel |
| Movement | 45-640, 45-660 | Brass and Nickel-silver with highly polished bear- ing surfaces. An internal zero stop is standard. |
|  | 45-740, 45-760 | Stainless Steel with highly polished bearing surfaces. An internal zero stop is standard. |
| Pointer | 600/700 Series (all) | Balanced micro-adjustable Aluminum, black finish |
| Dial | 600/700 Series (all) | Aluminum, white background with black scale. UV resistant. |
| Fill liquid ** | 45-660, 45-760 | Glycerin |

OPERATING SPECIFICATIONS

- Working Pressure Limitations

  - Dynamic Pressure

The working pressure should be limited to 60% of the dial range.

  - Static Pressure

The working pressure, where no sharp fluctuations occur, should be limited to 90% of the dial range

APPLICATIONS

  - Injection molding machines

  - Laboratory & test equipment

  - Power generation

  - Oil field & offshore

  - Utilities

  - Water & wastewater

Dial Indicating Pressure Gauges

Process

* For every 18 °F (10 °C) shift in temperature from which the gauge is calibrated, the user can experience up to ±0.4% additional error.

** See page 51 for gauge fill options.

For details on accuracy/standard dial configuration

and dial layouts, see pages 56-61.

26

NOSHOK 600 Series Gauges:

WARNING: This product can expose you to chemicals including Lead, which is known to the State of California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

NOSHOK 700 Series Gauges:

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GAUGE SIZES 45 4-1/2″ |  |  |  |  |  |  |  |  |
| CASE TYPES | 640 | Brass, dry, bottom connection | 660 | Brass, liquid filled, bottom connection |  |  |  |  |
|  | 740 | SS, dry, bottom connection | 760 | SS, liquid filled, bottom connection |  |  |  |  |
| PRESSURE | 30vac | -30 inHg to 0 psi | 30/300 | -30 inHg to 0 to 300 psi | 300 | 0 psi to 300 psi | 3000 | 0 psi to 3,000 psi |
| RANGES | 30/15 | -30 inHg to 0 to 15 psi | 15 | 0 psi to 15 psi | 400 | 0 psi to 400 psi | 5000 | 0 psi to 5,000 psi |
|  | 30/30 | -30 inHg to 0 to 30 psi | 30 | 0 psi to 30 psi | 600 | 0 psi to 600 psi | 6000 | 0 psi to 6,000 psi |
|  | 30/60 | -30 inHg to 0 to 60 psi | 60 | 0 psi to 60 psi | 800 | 0 psi to 800 psi | 10000 | 0 psi to 10,000 psi |
|  | 30/100 | -30 inHg to 0 to 100 psi | 100 | 0 psi to 100 psi | 1000 | 0 psi to 1,000 psi | 15000 | 0 psi to 15,000 psi |
|  | 30/160 | -30 inHg to 0 to 160 psi | 160 | 0 psi to 160 psi | 1500 | 0 psi to 1,500 psi |  |  |
|  | 30/200 | -30 inHg to 0 to 200 psi | 200 | 0 psi to 200 psi | 2000 | 0 psi to 2,000 psi |  |  |
| SCALE OPTIONS | psi | psi single scale | psi/kg/cm2 | psi/kg/cm2 dual scale | psi/bar | psi/bar dual scale |  |  |
| CONNECTION SIZES | 1/4 | 1/4″ NPT | 1/2 | 1/2″ NPT |  |  |  |  |
| OPTIONS | SG GL MIP BPMR | Safety Glass Lens Glass Lens Maximum Indicating Pointer Uninstalled Black Panel Mount Ring | CPMR OS LM ST | Uninstalled Chrome Panel Mount Ring Overload Stop Laser Marking Stainless Steel Tagging | BP3 BT3 ST8 | Brass Press Fit Orifice 0.3 mm Brass Threaded Orifice 0.3 mm 316SS Threaded Orifice 0.8 mm |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

NOTE: Refer to 600/700 Series Options & Accessories chart on page 52 for availability by part number.

EXAMPLE	45 – 740 – 100 – psi – 1/2 – ST8

Gauge size	.. 4-1/2"

Case type	SS internals, dry, bottom connection

Pressure range & scale option	psi to 100 psi

Connection size	1/2" NPT

Option	316SS Threaded Orifice 0.8 mm

45-640/660 & 45-740/760

5.83"	5.39"

(148 mm) (137 mm)

0.43"

(11 mm)

0.24"

(6 mm)

0.87"

(22 mm)

3.39"

(86 mm)

3.82"

5.08"

(129 mm)

1.06" (27 mm)

1.69" (43 mm)

(97 mm)

600/700 SERIES	INFORMATION

ORDERING

DIMENSIONS

3.46"

(88 mm)

5.83"	5.39"

(148 mm) (137 mm)

5.98"

(152 mm)

3.82"

(97 mm)

0.87"

(22 mm)

1.69" (43 mm)

45-640/660 & 45-740/760 Panel Mount  Ring

27

OPERATING SPECIFICATIONS

- Working Pressure Limitations

  - Static Pressure

The working pressure, where no sharp fluctuations occur, should be limited to 100% of the dial range. NOTE: 800 Series Precision Test gauges are not intended for dynamic applications.

APPLICATIONS

  - Aerospace equipment

  - Gauge repair facilities

  - Laboratory & test equipment

  - Precision measurement

SERIES

800

Highly accurate dry gauge

- Vacuum and compound ranges through 0 psi to 6,000 psi

- 6" gauge size

- Stainless Steel case

- Beryllium copper, 316 Stainless Steel, and Brass wetted parts

|  | SERIES SPECIFICATIONS |  |
| --- | --- | --- |
| Pressure ranges | 60-800 | Vacuum and compound ranges through 0 psi to 6,000 psi |
| Accuracy | 60-800 | ±0.25% full scale |
| Temperature ranges* | 60-800 | Media -40 °F to 180 °F (-40 °C to 80 °C) Ambient -40 °F to 140 °F (-40 °C to 60 °C) |
| Measuring element | 60-800 | Beryllium copper Bourdon tube to 1,000 psi 316 SS Bourdon tube 1,500 psi to 6,000 psi |
| Connection | 60-800 | 1/4″ NPT bottom connection, Brass |
| Case | 60-800 | 304 Stainless Steel |
| Cover ring | 60-800 | 304 Stainless Steel |
| Lens | 60-800 | Instrument glass |
| Pointer | 60-800 | Adjustable knife-edge pointer |
| Dial | 60-800 | Aluminum, white mirrored background with black scale. |
| Movement | 60-800 | Brass with jeweled bearings Nickel-silver pinion gear and shafts |

- For every 18 °F (10 °C) shift in temperature from which the gauge is calibrated, the user can experience up to ±0.4% additional error.

Dial Indicating Pressure Gauges

Precision Test

For details on accuracy/standard dial configuration

and dial layouts, see pages 56-61.

WARNING: This product can expose you to chemicals including Lead, which is known to the State of California to

28	cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GAUGE SIZE 60 6″ |  |  |  |  |  |  |  |  |
| CASE TYPE | 800 | SS Case, bottom connection |  |  |  |  |  |  |
| PRESSURE | 30vac | -30 inHg to 0 psi | 30/300 | -30 inHg to 0 to 300 psi | 300 | 0 psi to 300 psi | 5000 | 0 psi to 5,000 psi |
| RANGES | 30/15 | -30 inHg to 0 to 15 psi | 15 | 0 psi to 15 psi | 400 | 0 psi to 400 psi | 6000 | 0 psi to 6,000 psi |
|  | 30/30 | -30 inHg to 0 to 30 psi | 30 | 0 psi to 30 psi | 600 | 0 psi to 600 psi |  |  |
|  | 30/60 | -30 inHg to 0 to 60 psi | 60 | 0 psi to 60 psi | 1000 | 0 psi to 1,000 psi |  |  |
|  | 30/100 | -30 inHg to 0 to 100 psi | 100 | 0 psi to 100 psi | 1500 | 0 psi to 1,500 psi |  |  |
|  | 30/160 | -30 inHg to 0 to 160 psi | 160 | 0 psi to 160 psi | 2000 | 0 psi to 2,000 psi |  |  |
|  | 30/200 | -30 inHg to 0 to 200 psi | 200 | 0 psi to 200 psi | 3000 | 0 psi to 3,000 psi |  |  |
| SCALE OPTION | psi | psi single scale |  |  |  |  |  |  |
| CONNECTION SIZES |  | 1/4 1/4″ NPT | 1/2 1/2″ NPT |  | SST SAE J1926-3: 7/16-20 Adjustable |  |  |  |
| OPTIONS | SSFF SSRF GC LM | 304SS Front Flange 304SS Rear Flange Gauge Carrying Case Laser Marking | ST BP3 BT8 | Stainless Steel Tagging Brass Press Fit Orifice 0.3 mm Brass Threaded Orifice 0.8 mm |  |  |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

NOTE: Refer to 800 Series Options & Accessories chart on page 52 for availability by part number.

EXAMPLE	60 – 800 – 100 – psi – 1/4 – GC

Gauge size	6"

Case type	SS case, bottom connection

Pressure range & scale option	psi to 100 psi

Connection size	1/4" NPT

Option	Gauge Carrying Case

60-800* 60-800 Front Flange 60-800 Rear Flange

*1.95" (49.5 mm)

7.72" (196 mm)

0.12"

(3 mm)

*2.07" (52.5 mm)

6.34"

(161 mm)

4.61"

(117 mm)

0.87"

(22 mm)

*1.63" (41.5 mm)

0.31"

(8 mm)

6.34"

(161 mm)

4.61"

(117 mm)

0.87 "

(22 mm)

7.01" (178 mm)

4.61"

(117 mm)

6.34"

7.72" (196 mm)

7.01" (178 mm)

m)

0.23"

(58 mm)

(161 m

0.61" (15.5 mm)

0.87"

(22 mm)

120°

0.61" (15.5 mm)

120°

0.61" (15.5 mm)

800 SERIES	INFORMATION

ORDERING

DIMENSIONS

*For ranges ≤60 psi and ≥1,500 psi,

increase by 0.63" (16 mm)

##### 29

Dial Indicating Pressure Gauges

ABS & Stainless Steel Case, Liquid Filled

###### OPERATING SPECIFICATIONS

- Working Pressure Limitations

  - Dynamic Pressure

The working pressure should be limited to 60% of the dial range.

  - Static Pressure

The working pressure, where no sharp fluctuations occur, should be limited to 90% of the dial range

APPLICATIONS

  - Automotive

  - Construction

  - Hydraulics & pneumatics

  - Power generation

  - Transportation

  - Water management

For details on accuracy/standard dial configuration

and dial layouts, see pages 56-61.

30

SERIES

900

High quality liquid filled gauge

- Vacuum and compound ranges through 0 psi to 15,000 psi

- 1-1/2", 2", 2-1/2" and 4" gauge sizes

- Impact-resistant ABS and Stainless Steel case

- Copper alloy and Brass wetted parts

|  | SERIES SPECIFICATIONS |  |
| --- | --- | --- |
| Pressure ranges | 900 Series (all) | Vacuum and compound ranges through 0 psi to 15,000 psi |
| Accuracy | 15-910 | ±2.5% full scale |
|  | 25-900, 25-910, 25-901, 25-911 | ±1.6% full scale |
|  | 40-901, 40-911 | ±1% full scale |
| Temperature ranges* | 900 Series (all) | Media -4 °F to 140 °F (-20 °C to 60 °C) Glycerin fill -40 °F to 140 °F (-40 °C to 60 °C) Special fill Ambient -4 °F to 140 °F (-20 °C to 60 °C) Glycerin fill -40 °F to 140 °F (-40 °C to 60 °C) Special fill |
| Measuring element | 900 Series (up to 600 psi) | Copper alloy C-Type Bourdon tube |
|  | 900 Series (> 600 psi) | Coiled safety tube |
| Connection | 15-910 | 1/8″ NPT, Brass |
|  | 25-900, 25-910, 25-901, 25-911 | 1/4″ NPT or 7/16”-20 adjustable, Brass |
|  | 40-901, 40-911 | 1/4″ NPT, Brass 1/2″ NPT, Brass |
| Case | 15-910, 25-900, 25-910 | ABS with safety relief plug |
|  | 25-901, 25-911, 40-901, 40-911 | 304 Stainless Steel |
| Bezel | 25-901, 25-911, 40-901, 40-911 | 304 Stainless Steel |
| Lens | 15-910, 25-900, 25-910 | Acrylic; ultrasonically welded to the case |
|  | 25-901, 25-911, 40-901 | Polycarbonate |
| Pointer | 15-910, 25-900, 25-910, 25-901, 25-911 | Molded plastic |
|  | 40-901, 40-911 | Balanced Aluminum, black finish |
| Dial | 15-910, 25-900, 25-910, 25-901, 25-911 | Molded plastic, white background with black primary scale & red secondary scale. UV resistant |
|  | 40-901, 40-911 | Aluminum, white background with black primary scale & red secondary scale. UV resistant. |
| Movement | 15-910, 25-900, 25-910, 25-901, 25-911 | Brass and nylon with highly polished bearing surfaces |
| Fill liquid** | 15-910 | 86.5/13.5 Glycerin:H2O |

- For every 18 °F (10 °C) shift in temperature from which the gauge is calibrated, the user can experience up to ±0.4% additional error.

**See page 51 for gauge fill options.

WARNING: This product can expose you to chemicals including Lead, which is known to the State of California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

900 SERIES	INFORMATION

ORDERING

DIMENSIONS

| ORDERING INFORMATION |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GAUGE SIZES | 15 | 1-1/2″ | 20 | 2″ | 25 | 2-1/2″ 40 | 4″ |
| CASE TYPES | 900 901 | ABS Case, bottom connection SS Case, bottom connection |  |  | 910 911 | ABS Case, back connection SS Case, back connection |  |
| PRESSURE | 30vac | -30 inHg to 0 psi | 100 | 0 psi to 100 psi | 5000 | 0 psi to 5,000 psi 10 | 0 bar to 10 bar |
| RANGES | 30/15 | -30 inHg to 0 to 15 psi | 160 | 0 psi to 160 psi | 6000 | 0 psi to 6,000 psi 16 | 0 bar to 16 bar |
|  | 30/30 | -30 inHg to 0 to 30 psi | 200 | 0 psi to 200 psi | 7500 | 0 psi to 7,500 psi 25 | 0 bar to 25 bar |
|  | 30/60 | -30 inHg to 0 to 60 psi | 300 | 0 psi to 300 psi | 10000 | 0 psi to 10,000 psi 40 | 0 bar to 40 bar |
|  | 30/100 | -30 inHg to 0 to 100 psi | 400 | 0 psi to 400 psi | 15000 | 0 psi to 15,000 psi 60 | 0 bar to 60 bar |
|  | 30/160 | -30 inHg to 0 to 160 psi | 600 | 0 psi to 600 psi | −1 | −1 bar to 0 bar 100 | 0 bar to 100 bar |
|  | 30/200 | -30 inHg to 0 to 200 psi | 800 | 0 psi to 800 psi | 1 | 0 bar to 1 bar 160 | 0 bar to 160 bar |
|  | 30/300 | -30 inHg to 0 to 300 psi | 1000 | 0 psi to 1,000 psi | 1.6 | 0 bar to 1.6 bar 250 | 0 bar to 250 bar |
|  | 15 | 0 psi to 15 psi | 1500 | 0 psi to 1,500 psi | 2.5 | 0 bar to 2.5 bar 400 | 0 bar to 400 bar |
|  | 30 | 0 psi to 30 psi | 2000 | 0 psi to 2,000 psi | 4 | 0 bar to 4 bar 600 | 0 bar to 600 bar |
|  | 60 | 0 psi to 60 psi | 3000 | 0 psi to 3,000 psi | 6 | 0 bar to 6 bar 1000 | 0 bar to 1,000 bar |
| SCALE OPTIONS | psi psi/bar | psi single scale psi/bar dual scale | psi/kg/cm2 | psi/kg/cm2 dual scale | bar/psi | bar/psi dual scale psi/kPa | psi/kPa dual scale |
| CONNECTION SIZES | 1/8 | 1/8″ NPT | 1/4 | 1/4″ NPT | 1/2 | 1/2″ NPT SST | SAE J1926-3:7/16-20 Adjustable * |
| OPTIONS | PMC SPMC SSBU SSB | Steel Panel Mount Clamp 304SS Panel Mount Clamp Stainless Steel Bezel & U-clamp Stainless Steel Bezel | AP MIP SP SG | Adjustable Pointer Maximum Indicating Pointer Red Set Pointer Safety Glass Lens | SSFF SSRF LM ST | 304SS Front Flange BP3 304SS Rear Flange BT5 Laser Marking BT8 Stainless Steel Tagging | Brass Press Fit Orifice 0.3 mm Brass Threaded Orifice 0.5 mm Brass Threaded Orifice 0.8 mm |
|  | SSCR | 304SS Cover Ring | BLFF | Black Front Flange |  |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

NOTE: Refer to 900 Series Options & Accessories chart on page 53 for availability by series number.

* Includes FKM o-ring

EXAMPLE	25 – 910 – 1000 – psi /kPa – 1/4 – PMC

Gauge size	.. 2-1/2"

Case type	ABS case, liquid filled, back connection

Pressure range & scale option	0 psi to 1,000 psi/kPa

Connection size	1/4" NPT

Option	Panel Mount Clamp

25-900 25-901

2.13"

(54 mm)

2.83"

(72 mm)

2.13"

(54 mm)

0.55"

(14 mm)

0.45" (11.5 mm)

1.26"

(32 mm)

2.68"

(68 mm)

2.13"

(54 mm)

0.55"

(14 mm)

0.51" (13 mm)

##### 31

15-910 25-910 25-911

1.67"	 (42.5 mm)

1.61"

(41 mm)

0.47"

(12 mm)

1.04"	 (26.5 mm)

1.89"

(48 mm)

0.24" (6 mm)

1.85"

(47 mm)

0.20" (5 mm)

2.48"

(63 mm)

0.55"

2.68"

(68 mm)

2.45"

(62.2 mm)

0.55"

2.68"

(68 mm)

(14 mm)

(14 mm)

1.14"

(29 mm)

1.26"

(32 mm)

40-901 40-911

1.85"

(47 mm)

* 2.58"

(65.5 mm)	0.30"

(7.5 mm)

3.94"

(100 mm)

* 3.15"

(80 mm)

4.21"

(107 mm)

3.94"

(100 mm)  1.18"

(30 mm)

4.21"

(107 mm)

- 1/4" NPT shown

Add 6 mm for 1/2" NPT

0.61"

(15.5 mm)

0.87"

(22 mm)

0.87"

(22 mm)

1.85"

(47 mm)

25-910 Front Flange 25-911 Front Flange

1.73"

3.35" (85 mm)

2.95" (75 mm)

(44 mm)

0.39" (10 mm)

1.77"

2.95" (75 mm)

3.35" (85 mm)

(45 mm) 		 	0.28" (7 mm)

0.14" (3.6 mm)

0.55"

(14 mm)

2.48"

(63 mm)

0.14"

(3.6 mm)

0.55"

(14 mm)

2.45"

(62.2 mm)

Dial Indicating Pressure Gauges

Dimensions

120°

##### 32

1.14"

(29 mm)

120°

1.26"

(32 mm)

40-911 Front Flange 40-901 Rear Flange

5.20" (132 mm)

4.57" (116 mm)

2.53" (64.2 mm)

0.35"

(8.8 mm)

5.20" (132 mm)

0.08"

(2 mm)

1.93"

(49 mm)

4.21"

(107 mm)

3.15"

(80 mm)

0.69"

0.87"

(22 mm)

4.57" (116 mm)

0.19"

(4.8 mm)

1.18"

(30 mm)

4.21"

(107 mm)

0.14 " (3.6 mm)

120°

0.87"

(22 mm)

1.85"

(47 mm)

120°

(17.5 mm)

40-911 Rear Flange 25-911 Flange Ring

0.14" (3.6 mm)

0.08"

5.20" (132 mm)

4.57" (116 mm)

(2 mm)

1.18"

(30 mm)

1.93"

(49 mm)

4.21"

(107 mm)

2.45"

3.35" (85 mm)

(62.2 mm)

2.05"

(52 mm)

0.55"

(14 mm)

0.98"	 	 0.28"

120°

2.87"

(73 mm)

(25 mm)

(7 mm)

25-910 Panel Mount Clamp 25-911 Panel Mount Clamp

1.89"

(48 mm)	 		 	0.24" (6 mm)

1.85"

(47 mm) 		 	0.20" (5 mm)

2.45"

(62.2 mm)

2.68"

(68 mm)

2.45"

(62.2 mm)

2.68"

(68 mm)

900 SERIES	DIMENSIONS

1.14"

(29 mm)

1.26"

(32 mm)

##### 33

1000 SERIES

##### Simple, rugged, compact differential pressure gauge

  - Ranges from 0 psid to 5 psid through 0 psid to 110 psid

  - 2-1/2", 4-1/2" and 6" gauge sizes

  - Engineered plastic gauge case

  - Clear anodized Aluminum and 316 Stainless Steel wetted parts

SPECIFICATIONS

Pressure ranges	0 psid to 5 psid through 0 psid to 110 psid

Max. working static pressure	Aluminum 3,000 psig; Stainless Steel 6,000 psig

Accuracy	±3/2/3% of full scale on rising pressure

APPLICATIONS

  - Heat exchangers

  - Filter monitoring

Temperature ranges (Including switch option)

Temperature ranges

(4-20 mA transmitter option)

Media -40 °F to 200 °F (-40 °C to 93 °C)

Ambient -40 °F to 200 °F (-40 °C to 93 °C)

Storage -40 °F to 200 °F (-40 °C to 93 °C)

Ambient -20 °F to 150 °F (-29 °C to 66 °C)

  - Flow indication

  - Level indication

Measuring element	316 Stainless Steel and ceramic piston/magnet

O-ring & diaphragm material	NBR

Connection	1/4” NPT female, back connection

Sensor housing material	Clear anodized Aluminum

Case	Engineered plastic

Bezel	Engineered plastic

Lens	Shatter-resistant acrylic

Pointer	Balanced Aluminum, black finish

Dial	Aluminum, white background with black scale

Movement	Magnetic

Optional switch rating

SPDT, 3W, 0.25 Amp, 125 Vac/Vdc (standard) (switch adjustable range of 15-95%). Other options available, consult factory.

Differential Pressure Gauges

Piston Type

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

34	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

1000 SERIES	INFORMATION

ORDERING

DIMENSIONS

| ORDERING INFORMATION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GAUGE SIZES & SERIES | 25 - 10 | 2-1/2″ | 45 - 10 | 4-1/2″ | 60 - 10 | 6″ |  |  |
| CONNECTION LOCATIONS | 0 | Bottom | 1 | Back | 2 | Side |  |  |
| CONNECTION SIZE | 2 | 1/4″ NPT female | 9 | 7/16-20 female (Back only) |  |  |  |  |
| PRESSURE RANGES * | P5 P10 P15 | 0 psid to 5 psid 0 psid to 10 psid 0 psid to 15 psid | P20 P25 P30 | 0 psid to 20 psid 0 psid to 25 psid 0 psid to 30 psid | P50 P60 P75 | 0 psid to 50 psid 0 psid to 60 psid 0 psid to 75 psid | P100 P110 | 0 psid to 100 psid 0 psid to 110 psid |
| SENSOR HOUSING MATERIALS | A | Aluminum (3,000 max working pressure) |  |  | S | 316L Stainless Steel (6,000 max working pressure) |  |  |
| O-RING & DIAPHRAGM | 1 | PTFE | 3 | NBR |  |  |  |  |
| MATERIALS | 2 | FKM | 4 | EPDM |  |  |  |  |
| CASE MATERIALS | A | Aluminum (4-1/2" only) | P | Engineered plastic |  |  |  |  |
| LENSES | 1 | Shatter-resistant acrylic | 2 | Safety glass ** | 3 | Maximum indicating pointer (MIP) *** |  |  |
| FILL FLUID (optional) | GY | Glycerin | SL | Silicone † |  |  |  |  |
| SWITCH OR TRANSMITTER TYPE | 1 | Single switch, flying leads with grommet wire seal |  |  | 5 | Single switch with Hirschman electrical connection |  |  |
| & HOUSING | 2 | Dual switch, flying leads with grommet wire seal |  |  | 6 | Dual switch with Hirschman electrical connection |  |  |
|  | 3 | Single switch, flying leads with 1/4" female NPT, NEMA 4X |  |  | 7 | 4-20 mA transmitter in NEMA 4x IP65 plastic enclosure with terminal |  |  |
|  | 4 | Dual switch, flying leads with 1/4" female NPT, NEMA 4X |  |  |  | strip (1/2" female NPT conduit connection) |  |  |
| OPTIONS | MH MK5-CS MK5-SS | (2) 1/4-20 Mounting Holes Pipe Mounting Kit, Steel Pipe Mounting Kit, Stainless Steel |  |  | RP ST WMK | Reversed Ports Stainless Steel Tagging Wall Mounting Kit |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

- Other ranges and scales available on request.

** Only available with dry, 4-1/2" gauge size with Aluminum case.

*** Available with dry gauge only, 2-1/2" and 4-1/2" gauge sizes only.

†	Optional Silicone filling available with 2-1/2" and 6" gauge case sizes, and 4-1/2" gauge case size with Aluminum case and standard shatter-resistant acrylic lens only.

EXAMPLE	25-10 1 2 – P5 – A 2 P – 1

Gauge size & series	.. 2-1/2" 1000 Series

Connection location	Back

Connection size	1/4" NPT female

Pressure range	0 psid to 5 psid

Sensor housing material	Aluminum, clear

O-ring material	FKM

Case material	Engineered plastic

Lens	Shatter-resistant acrylic

35

2-1/2" Gauge

1.42"

(36.0 mm)

0.12" (3.1 mm)

3.39"

(86.0 mm)

3.29"

(83.5 mm)

3.29" (83.5 mm)

1.00"

(25.4 mm)

Ø3.00" (76.1 mm)

1.25"

(31.8 mm)

2.00"

(50.7 mm)

2.12"

(53.8 mm)

4.0"

(102 mm)

0.50"

(12.7 mm)

4-1/2" Gauge

Ø6.30" (Ø160.0 mm)

1.25" (31.8 mm)

0.14" (3.6 mm)

1.00" (25.4 mm)

Ø5.22" (132.5 mm)

1.47"

(37.3 mm)

1.72" (43.6 mm)

2.43"

(61.7 mm)

2.12"

(53.8 mm)

3.39" (86.0 mm)

4.0" (102 mm)

6" Gauge

Ø8.18" (Ø207.6 mm)

1.25" (31.8 mm)

0.15" (3.8 mm)

1.00"

(25.4 mm)

Ø6.95" (176.4 mm)

2.12"  (53.8 mm)

3.39" (86.0 mm)

4.0" (102 mm)

1.55"

(39.4 mm)

Differential Pressure Gauges

Dimensions

2.04" (51.7 mm)

##### 36

2.98"

(75.8 mm)

1000 SERIES

Single switch, flying leads with grommet wire seal			Dual switch, flying leads with grommet wire seal

Single switch, flying leads with 1/4" female NPT, NEMA 4X			Dual switch, flying leads with 1/4" female NPT, NEMA 4X

Single switch with Hirschman electrical connection			Dual switch with Hirschman electrical connection

4-20 mA transmitter in NEMA 4x IP65 plastic enclosure with terminal strip (1/2" female NPT conduit connection)

37

1100 SERIES

##### Simple, rugged, compact differential pressure gauge

  - Ranges from 0 inH2O to 20 inH2O through 0 psid to 100 psid

  - 2-1/2", 4-1/2" and 6" gauge sizes

  - Engineered plastic gauge case

  - Black anodized Aluminum and 316 Stainless Steel wetted parts

SPECIFICATIONS

Pressure ranges	0 inH2O to 20 inH2O through 0 psid to 100 psid

Max. working static pressure	Aluminum & Stainless Steel 3,000 psig; Brass 1,500 psig

Accuracy	±3/2/3% of full scale on rising pressure

APPLICATIONS

  - Heat exchangers

Temperature ranges (Including switch option)

Temperature ranges

Media -40 °F to 200 °F (-40 °C to 93 °C)

Ambient -40 °F to 200 °F (-40 °C to 93 °C)

Storage -40 °F to 200 °F (-40 °C to 93 °C)

Ambient -20 °F to 150 °F (-29 °C to 66 °C)

  - Filter monitoring

  - Flow indication

  - Level indication

(4-20 mA transmitter option)		 Measuring element	316 Stainless Steel and ceramic magnet

O-ring & diaphragm material	NBR

Connection	1/4” NPT female, back connection

Sensor housing material	Black anodized Aluminum

Case	Engineered plastic

Bezel	Engineered plastic

Lens	Shatter-resistant acrylic

Pointer	Balanced Aluminum, black finish

Dial	Aluminum, white background with black scale

Movement	Magnetic

Optional switch rating

SPDT, 3W, 0.25 Amp, 125 Vac/Vdc (standard) (switch adjustable range of 15-95%). Other options available, consult factory.

Differential Pressure Gauges

Diaphragm Type

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

38	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

1100 SERIES	INFORMATION

ORDERING

DIMENSIONS

| ORDERING INFORMATION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GAUGE SIZES & SERIES | 25 - 11 | 2-1/2″ | 45 - 11 | 4-1/2″ | 60 - 11 | 6″ |  |  |
| CONNECTION LOCATIONS | 0 | Dual top & bottom *** | 1 | Back | 2 | Side | 3 | Bottom |
| CONNECTION SIZE | 2 | 1/4″ NPT female | 9 | 7/16-20 female (Back or side only) |  |  |  |  |
| PRESSURE RANGES* | W20 | 0 inH2O to 20 inH2O | W75 | 0 inH2O to 75 inH2O | W400 | 0 inH2O to 400 inH2O | P30 | 0 psid to 30 psid |
|  | W25 | 0 inH2O to 25 inH2O | W100 | 0 inH2O to 100 inH2O | P5 | 0 psid to 5 psid | P50 | 0 psid to 50 psid |
|  | W30 | 0 inH2O to 30 inH2O | W135 | 0 inH2O to 135 inH2O | P10 | 0 psid to 10 psid | P60 | 0 psid to 60 psid |
|  | W40 | 0 inH2O to 40 inH2O | W150 | 0 inH2O to 150 inH2O | P15 | 0 psid to 15 psid | P75 | 0 psid to 75 psid |
|  | W50 | 0 inH2O to 50 inH2O | W200 | 0 inH2O to 200 inH2O | P20 | 0 psid to 20 psid | P100 | 0 psid to 100 psid |
|  | W60 | 0 inH2O to 60 inH2O | W300 | 0 inH2O to 300 inH2O | P25 | 0 psid to 25 psid |  |  |
| SENSOR HOUSING MATERIALS | A | Aluminum, black | B | Brass | S | 316L Stainless Steel |  |  |
| O-RING & DIAPHRAGM MATERIALS | 2 | FKM | 3 | NBR | 4 | EPDM |  |  |
| CASE MATERIAL | A | Aluminum (4-1/2" only) | P | Engineered plastic |  |  |  |  |
| LENSES | 1 | Shatter-resistant acrylic | 2 | Safety glass** | 3 | Maximum indicating pointer (MIP) † |  |  |
| FILL FLUIDS (optional) | GY | Glycerin | SL | Silicone † † |  |  |  |  |
| SWITCH OR TRANSMITTER TYPE & HOUSING (OPTIONAL) | 3 4 | Single switch, NEMA 4X Dual switch, NEMA 4X |  |  | 7 | 4-20 mA transmitter in NEMA 4x IP65 plastic enclosure with terminal strip (1/2" female NPT conduit connection). |  |  |
| OPTIONS | MH MK5-CS MK5-SS | (2) 1/4-20 Mounting Holes Pipe Mounting Kit, Steel Pipe Mounting Kit, Stainless Steel |  | RP ST WMK |  | Reversed Ports Stainless Steel Tagging Wall Mounting Kit |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

* Other ranges and scales available on request.

** Only available with dry, 4-1/2" gauge size with Aluminum case.

*** Not available with switch or transmitter option.

† Available with dry gauge only, 2-1/2" and 4-1/2" gauge sizes only.

† † Optional Silicone filling available with 2-1/2" and 6" gauge case sizes, and 4-1/2" gauge case size with Aluminum case and standard shatter-resistant acrylic lens only.

EXAMPLE	25-11 1 2 – P75 – A 2 P – 1

Gauge size & series	.. 2-1/2" 1100 Series

Connection location	Back

Connection size	1/4" NPT female

Pressure range	0 psid to 75 psid

Sensor housing material	Aluminum, black

O-ring material	FKM

Case material	Engineered plastic

Lens	Shatter-resistant acrylic

39

1.30"

(71.1 mm)

3.85"

(97.8 mm)

4.4"

(112 mm)

2.00"		 		 0.12" (50.8 mm)				(3.1 mm)

2.00"

(50.8 mm)

Ø3.00" (76.1 mm)

2.19"

(55.7 mm)

2.78"

(70.7 mm)

| (33.0 mm) |  |  |  |
| --- | --- | --- | --- |
|  | 2.80" |  |  |

2-1/2" Gauge  (<25 psid)

3.29"

(83.5 mm)

3.29" (83.5 mm)

0.04"

(1.1 mm)

4-1/2" Gauge (<25 psid)

Ø6.30" (Ø160.0 mm)

2.00 (50.8 mm)

0.14" (3.6 mm)

1.30" (33.0 mm)

2.00" (50.8 mm)

Ø5.22" (132.5 mm)

1.02"

(25.8 mm)

2.47"

(62.7 mm)

3.20"

(81.3 mm)

2.80"

(71.1 mm)

3.85" (97.8 mm)

4.4" (112 mm)

1.30" (33.0 mm)

2.80"

(71.1 mm)

3.85" (97.8 mm)

4.4" (112 mm)

6" Gauge (<25 psid)

Ø8.18" (Ø207.6 mm)

2.00 (50.8 mm)

0.15" (3.8 mm)

2.00" (50.8 mm)

Ø6.95" (176.4 mm)

1.10"

(27.9 mm)

Differential Pressure Gauges

Dimensions

2.79"

(70.9 mm)

3.74"

40	(94.9 mm)

3.80"

(96.5 mm)

4.70"

(119.4 mm)

5.27"

(133.8 mm)

2-1/2" Gauge  (≥25 psid)

3.29"

(83.5 mm)

3.29" (83.5 mm)

2.00"

(50.8 mm)

0.12"

(3.1 mm)

2.00"

(50.8 mm)

Ø3.00" (76.1 mm)

2.19"

(55.7 mm)

2.72"

(69.1 mm)

0.04"

(1.1 mm)

4-1/2" Gauge (≥25 psid)

Ø6.30" (Ø160.0 mm)

2.00 (50.8 mm)	 	 	0.14" (3.6 mm)

2.00" (50.8 mm)

Ø5.22" (132.5 mm)

1.02"

(25.8 mm)

2.47"

(62.7 mm)

3.20"

(81.3 mm)

3.80"

(96.5 mm)

4.70" (119.4 mm)

5.27" (133.8 mm)

6" Gauge (≥25 psid)

Ø8.18" (Ø207.6 mm)

2.00 (50.8 mm)

2.00" (50.8 mm)

0.15" (3.8 mm)

Ø6.95" (176.4 mm)

1.10"

3.80"

(96.5 mm)

4.70" (119.4 mm)

5.27" (133.8 mm)

(27.9 mm)

2.79"

(70.9 mm)

3.74"

(94.9 mm)

1100 SERIES	DIMENSIONS

4-20 mA Transmitter  in NEMA 4x Enclosure

Single Switch  in NEMA 4x Enclosure

41

Differential Pressure Gauges

Dial Layouts

1000 Series 2-1/2"

1000 Series 4-1/2"

1100 Series 2-1/2"

42

1100 Series 4-1/2"

1100 Series 4-1/2"

43

APPLICATIONS

- Food & beverage processing

- Pasteurization systems

- Pharmaceutical

- Medical

10 SERIES

##### 3/4" clamp, dry gauge

- Ranges from 0 psig to 30 psig through 0 psig to 600 psig

- 2" gauge size

- Electropolished Stainless Steel case

- 316 Stainless Steel wetted parts

- Meets current standards for 3A and ASME BPE-2009

- C.I.P, S.I.P and Autoclave (only dry gauges are recommended for

Autoclave)

SPECIFICATIONS

Pressure ranges	0 psig to 30 psig through 0 psig to 600 psig

Accuracy	±2.5% full scale

Temperature ranges	Media -40 °F to 300 °F (-40 °C to 150 °C)

Ambient 25 °F to 140 °F (-4 °C to 60 °C)

Storage 25 °F to 140 °F (-4 °C to 60 °C)

Measuring element	316 Stainless Steel Bourdon tube

Connection	3/4" ASME-BPE Sanitary Clamp, 316L Stainless Steel

Diaphragm 316L Stainless Steel, electropolished to 32 μin Ra or better

Case	2" Electropolished 304 Stainless Steel

Cover ring	Electropolished 304 Stainless Steel

Lens*	Polycarbonate

Pointer	Balanced Aluminum, black finish

Dial	Aluminum, white background, black print

Movement	Stainless Steel

Fill liquid	Glycerin, USP Grade

*Note: Autoclave requires the addition of optional laminated safety glass lens

Diaphragm seal must be installed facing downward or in a vertical position for drainability. Do not install diaphragm seal facing in an upward position.

Sanitary Pressure Gauges

Fractional

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

44	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

10 SERIES	INFORMATION

ORDERING

DIMENSIONS

| ORDERING INFORMATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| SERIES | 100 | 10 Series fractional |  |  |
| CLAMP SIZE | 06 | 3/4″ |  |  |
| FILL LIQUID | 1 | Glycerin | Other food grade quality fill fluids available – please consult factory |  |
| GAUGE SIZE | 20 | 2″ |  |  |
| PRESSURE RANGES | 43 | 0 psig to 30 psig | 55 | 0 psig to 160 psig 64 0 psig to 400 psig |
|  | 46 | 0 psig to 60 psig | 58 | 0 psig to 200 psig 70 0 psig to 600 psig |
|  | 49 | 0 psig to 100 psig | 61 | 0 psig to 300 psig |
| OPTIONS | 0 | None | 3 | Safety Glass Lens (Required for Autoclave applications) |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

EXAMPLE	100  –  06  –  1  –  20  –  43  –  3

Series	10 Series fractional

Clamp size	3/4" ASME-BPE Sanitary

Fill liquid	Glycerin (USP food grade)

Gauge size	2"

Pressure range	0 psig to 30 psig

Option	Safety Glass Lens

2" Gauge with 3/4" ASME-BPE Sanitary Clamp Connection

0.378"

(9.6 mm)

1.043"

(26.5 mm)

1.969"

(50 mm)

2.067"

(52.5 mm)

0.551"

(14 mm)

Square

0.158"

(4 mm)

0.394"

(10 mm)

0.551"

(14 mm)

0.984"

(25 mm)

##### 45

###### APPLICATIONS

- Food & beverage processing

- Pasteurization systems

- Pharmaceutical

- Medical

10 SERIES

##### 1-1/2" and 2" clamp, fillable dry or liquid-filled gauge

- Ranges from -30 inHg to 0 psig through 0 psig to 600 psig

- 2-1/2" and 4" gauge sizes

- Electropolished Stainless Steel case

- 316 Stainless Steel wetted parts

- Meets current standards for 3A and ASME BPE-2009

- C.I.P, S.I.P and Autoclave (only dry gauges are recommended for

Autoclave)

SPECIFICATIONS

Pressure ranges	-30 inHg to 0 psig through 0 to 600 psig

Accuracy	2-1/2" gauge ±1.6% full scale 4" gauge ±1.0% full scale

Temperature ranges	Media -40 °F to 300 °F (-40 °C to 150 °C)

Ambient 25 °F to 140 °F (-4 °C to 60 °C)

Storage 25 °F to 140 °F (-4 °C to 60 °C)

Measuring element	316 Stainless Steel “C” tube

Connection	1-1/2" or 2" ASME-BPE Sanitary Clamp, 316L Stainless Steel

Diaphragm 316L Stainless Steel, electropolished to 32 μin Ra or better

Case	Electropolished  304 Stainless Steel

Bayonet ring	Electropolished  304 Stainless Steel

Lens	Safety glass

Pointer	Balanced Aluminum, black finish

Dial	Aluminum, white background, black print

Movement	Stainless Steel

Fill liquid	Glycerin, USP Grade

*Note: Autoclave requires the addition of optional laminated safety glass lens

Diaphragm seal must be installed facing downward or in a vertical position for drainability. Do not install diaphragm seal facing in an upward position.

Sanitary Pressure Gauges

Heavy-Duty

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

46	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |
| --- | --- | --- |
| SERIES | 100 | 10 Series heavy-duty, bottom connected 101 10 Series heavy-duty, back connected |
| CLAMP SIZES | 12 | 1-1/2″ 16 2″ |
| FILL LIQUID | 1 | Glycerin Other food grade quality fill fluids available – please consult factory |
| GAUGE SIZES | 25 | 2-1/2″ 40 4″ |
| PRESSURE RANGES | 01 | -30 inHg to 0 psig * 16 -30 inHg to 160 psig 46 0 psig to 60 psig 64 0 psig to 400 psig |
|  | 04 | -30 inHg to 15 psig 19 -30 inHg to 200 psig 49 0 psig to 100 psig 70 0 psig to 600 psig |
|  | 07 | -30 inHg to 30 psig 22 -30 inHg to 300 psig 55 0 psig to 160 psig |
|  | 10 | -30 inHg to 60 psig 40 0 psig to 15 psig * 58 0 psig to 200 psig |
|  | 13 | -30 inHg to 100 psig 43 0 psig to 30 psig 61 0 psig to 300 psig |
| GAUGE FILLS | 0 | None 1 Glycerin 2 Silicone 3 Mineral oil (All food grade quality fill fluids) |
| GAUGE OPTIONS | 0 | None 1 Max. Indicating Pointer 2 Adjustable Pointer ** |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

* Not available on 4″ gauge and 1-1/2″ ASME-BPE Sanitary Clamp

** Not available on 2-12" gauge

EXAMPLE	100 – 12 – 1 – 25 – 55 – 1 – 1

Series	10 Series heavy-duty

Clamp size	..1-1/2" ASME-BPE Sanitary

Fill liquid	Glycerin (USP food grade)

Gauge size	.. 2-1/2"

Pressure range	0 psig to 160 psig

Gauge fill	Glycerin

0.866"

(22 mm)

Square

0.112"

(2.85 mm)

1.90"

(48 mm)

1.125"

( 29 mm)

2.516"

(64 mm)

1.97" (50 mm)

4.01"

(102 mm)

0.680"

(17.3 mm)

4.61"

(117 mm)

0.866"

(22 mm)

Square

6"

mm)

1.40"

(36 mm)

1.375"

( 35 mm)

1.984"

(50 mm)

Option	Maximum Indicating Pointer

4" Gauge with 2" ASME-BPE Sanitary Clamp Connection 4" Gauge with 1-1/2" ASME-BPE Sanitary Clamp Connection

1.97" (50 mm)

4.01"

(102 mm)

0.680"

(17.3 mm)

4.61"

(117 mm)

0.11

(2.95

2-1/2" Gauge with 2" ASME-BPE Sanitary Clamp Connection 2-1/2" Gauge with 1-1/2” ASME-BPE Sanitary Clamp Connection

1.303"

(33 mm)

1.303"

2.504"

(63.6 mm)

3.189"

(81 mm)

0.55

(140

Squa

0.116"

(2.95 mm)

1.375"

(35 mm)

1.40"

(	)

36 mm

1.969"

(50 mm)

1.984"

(50 mm)

(33 mm)

0.112"

0.551"

(140 mm)

Square

2.504"

(63.6 mm)

1"

mm)

re

(2.85 mm)

1.90"

(48 mm)

2.516"

(64 mm)

1.125"

(29 mm)

0.374"

(9.5 mm)

3.189"

(81 mm)

0.374"

(9.5 mm)

10 SERIES	INFORMATION

ORDERING

DIMENSIONS

47

PANEL MOUNTING FLANGES

- Many panel mounting options are available and can be installed in the field

- Options include:

  - Brass Front Flanges (BFF)

  - Black Painted Steel Front Flanges (BLFF)

  - Chrome Front Flanges (CFF)

  - Stainless Steel Front Flanges (SSFF)

  - Chrome Triangular Bezel with U-Clamp (CBU)

  - Black Painted Steel Triangular Bezels with U-Clamp (BBU-Clamp)

  - Stainless Steel Narrow Bezel Front Flanges (SSBU)

  - Panel Mount Clamps (PMC)

- Chrome-plated Steel Adapter Rings (AR) are available in conjunction with several

of these flanges to adapt to oversized panel cut outs, including:

  - Stainless Steel Flange Rings (SSFR)

  - Chrome-Plated Steel Flange Rings (CFR)

  - Black or Chrome Panel Mount Rings (BPMR & CPMR)

- Rear Flanges (RF) for front of panel mounting are also available as a factory installed option on some series

CASES & COVER RINGS

- The following cases and cover rings are available on many NOSHOK gauges as production options:

  - Black painted Steel (BCR)

  - Chrome-plated Steel (CCR)

  - 304 Stainless Steel (SSCR)

- Some NOSHOK gauges are also available with a solid front, safety case

LENSES

- A variety of lens options are available on many NOSHOK gauges as a production option:

  - Instrument glass lenses

  - Laminated safety glass lenses

  - Acrylic lenses

  - Homalite lenses (resistant to many industrial solvents)

  - A Steel or Stainless case and cover ring may be required when other than

acrylic lenses are utilized

MAXIMUM INDICATING POINTERS (MIP)

- An invaluable tool for identifying pressure spikes in a system

- Extremely helpful during system start up and troubleshooting

- MIPs add an additional ±1% error to the gauge because of the increased load on the

Bourdon tube

- On ranges of 60 psi and lower, MIPs may double the allowed error of the gauge

Panel Mount Clamp 20-110 PMC

Chrome Triangular Bezel with U-Clamp

Cases and Cover Rings

Maximum Indicating Pointer

Dial Indicating Gauge Options & Accessories

See the Gauges Accessories & Options Charts on pgs. 50-53 for availability on specific gauges

48

SET POINTERS (SP)

  - Used to identify an operating minimum or maximum pressure or vacuum value

  - Set pointers are available on many NOSHOK gauges

RUBBER CASE PROTECTORS (RCP)

  - Ideal for gauges that are subjected to direct physical shock

  - 2-1/2" covers are blue and 4" covers are black

ORIFICES

  - Press-fit or threaded orifices in Brass or 316 Stainless Steel are available on

all NOSHOK pressure gauges

  - Available with I.D.’s from 0.004” to 0.032” depending on the specific NOSHOK gauge

  - Used in a gauge to restrict the flow of rapidly increasing and decreasing

pressures, reducing the immediate effect of pulsations and pressure spikes

  - Recommended for all dynamic applications

RECALIBRATORS & ADJUSTABLE POINTERS

  - This option gives the user the capability of resetting the pointer by an adjustment screw accessible through the dial, or by a gear located on the pointer

OVERPRESSURE PROTECTION

  - Overpressure protection of 3 times up to 10 times of the dial range is available on some NOSHOK gauges as a production option

AMMONIA REFRIGERATION GAUGES

  - Ammonia and refrigeration gauges with dials reading in both pressure and temperature are available in 400/500 Series 2-1/2” and 4" sizes

  - Refrigeration gauges with dials reading in pressure and temperature are available in 300, 400 and 500 Series for R-12 and R-22

LIQUID FILLING OPTIONS

  - Many NOSHOK gauges are available with liquid filling options

  - Standard fill is Glycerin

  - Optional fill liquids include Dow Corning 200® Silicone and Halocarbon®

SPECIAL CONNECTIONS

  - Available on most NOSHOK gauges

  - Some examples include:

    - Metric threads

    - Female threads

    - Straight threads (flare or swivel type)

    - Special o-ring connections

  - Please contact us with your requirements for prices, availability and minimum quantities

REID VAPOR TEST GAUGES

  - Configuration includes a handle, special dial and special pressure port

  - Available in 600/700 Series gauges with pressure ranges of 0 to 5 psi, 0 to 15 psi and 0 to 30 psi

Set Pointers

Rubber Case Protectors

Ammonia Gauges

See the Gauges Accessories & Options Charts on pgs. 50-53 for availability on specific gauges

49

Dial Indicating Gauge Options & Accessories

METRIC DIALS & CUSTOMIZED SPECIAL DIALS

- Dual scale metric dials in psi/bar, psi/kPa and psi/kg/cm2 are available on many NOSHOK gauges

- Other scales are available for specific sizes and ranges, such as single scale bar and kPa,

refrigerant scales and altitude scales

- Please consult the factory for availability

- Customized special dials such as non-standard metric scale, tons of ram, lbs. of force, etc.

are available in small quantities (as few as one piece) on some NOSHOK gauges

Metric Dials and Customized Special Dials

CERTIFIED CALIBRATION

- Available on all NOSHOK gauges

- Certified calibration provides the user with a serial numbered gauge along with a calibration sheet

against a primary pressure standard

- Traceable to the National Institute of Standards and Technology

50

MAGNETIC SPRING CONTACT SWITCH (MSCS)

  - An excellent choice when an accurate pressure switch is required in addition to a reliable

pressure gauge

  - Fully adjustable by the user

  - These switches are actuated by the pressure gauge pointer to provide accurate field adjustment

  - A removable adjustment key makes them tamper-proof

  - They operate with an extremely broad power supply, AC or DC up to 250V max. (30W 50 VA), allowing them to be used virtually anywhere in the world in addition to very remote applications with only DC battery pack power available

  - Standard units consist of (2) two magnetic spring switches; either one or both switches may be used:

    - Switch (1) one is normally closed

    - Switch (2) two is normally open with operation referenced on clockwise pointer motion

  - Magnetic spring contact switches are available as a factory installed option on 40-400 Series and 40-410 Series

  - The lowest full scale pressure range this switch may be used on is 0 psi to 60 psi because of the increased load on the pointer and Bourdon tube

  - A mating 4-pin connector with 5' of 4-wire and color coded shielded cable is standard

APPLICATIONS

SPECIFICATIONS

Type of power	A.C. or D.C. 24 to 250V max

Maximum amps	1.0 A

- Air compressors

- Gas compressors

Maximum switching capacity

30 W/50 VA

- Hydraulic and pneumatic circuitry

- Die-cast machinery

Gauge accuracy	Add an additional ±2%

Minimum magnet	1g

holding force

- Plastic injection molding machinery

Contact pin material	Silver Tungsten

40-400 Series Gauge with

Ambient temperature limitation

Minimum full scale pressure range

0 °F to 140 °F (-18 °C to 61 °C)

  - psi

Magnetic Spring Contact Switch

2

4

1

3

CONTACT NO. 2

Normally open, Closes on Rising Pressure

CONTACT NO. 1

Normally closed, Opens on Rising Pressure

G

WIRING AND TERMINAL LOCATION

    - Contact Switch No. 1; Red or Black

    - Contact Switch No. 2; Blue

    - Power; Green or Brown

    - Ground; Yellow/Green Stripe

##### 51

100 SERIES ABS & Steel CASE, DRY PRESSURE GAUGE ACCESSORIES

—    =	Option/accessory is available	C = Consult factory for availability	STD = Standard stock series specification

| MODEL NO. | 15-100 | 15-110 | 15-120 | 20-100 | 20-110 | 20-120 | 20-148 | 25-100 | 25-110 | 25-120 | 40-100 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CONNECTION |  |  |  |  |  |  |  |  |  |  |  |
| Black Steel Case (BSC) | C |  | STD | C | C | STD | — |  |  | STD |  |
| Chrome Case (CRC) | C |  | — | C | C | — | — |  |  | — | — |
| Flat Sided ABS Case (FAC) | — |  | — | — |  | — | — | — |  | — | — |
| Stainless Steel Case (SSC) | C |  | — | C | C | — | — |  |  | — | — |
| Silicone Dampened Movement (SDM) | C | C | C | C | C | C | C | C | C | C | C |
| Glass Lens (GL)* | C | N/C |  | C | N/C |  | — | N/C | N/C |  | N/C |
| Homalite Lens (HL)* | — | — |  | — | — |  | — | — | — |  | — |
| Polycarbonate Lens (LL)* | — | — | — | — | — | — | — |  |  | — | — |
| Maximum Indicating Pointer (MIP) | — | — | — | — | — | — | — | C | C | — | — |
| Red Set Pointer (SP)** |  | C | C | C |  | C |  |  |  | C | — |
| Safety Glass Lens (SG)* | — | — | — | — | — | — | — |  |  | — |  |
| Black Front Flange (BLFF) ABS Case | — |  | — | — |  | — | — | — |  | — | — |
| Chrome Front Flange (CFF) ABS Case | — |  | — | — |  | — | — | — |  | — | — |
| Chrome Front Flange (SCFF) Steel Case | C | C | — | C | C | — | — |  |  | — |  |
| Black Front Flange (SBFF) Steel Case | C | C | — | C | C | — | — |  |  | — |  |
| Black Rear Flange (BLRF) | — | — | — | — | — | — | — |  | — | — |  |
| Black Cover Ring (BCR)** | C |  | — | C | C | — | — |  |  | — |  |
| Stainless Steel Cover Ring (SSCR)** | C |  | — | C | C | — | — |  |  | — | — |
| Chrome Cover Ring (CCR)** | C |  | — | C | C | — | — |  |  | — |  |
| Polished Stainless Steel Bezel (SSB) | — |  | STD | — |  | STD | — | — |  | STD | — |
| Chrome Adaptor Ring (AR) | — |  |  | — |  |  | — | — |  |  | — |
| Panel Mount Clamp (PMC) | — |  | STD | — |  | STD | — | — |  | STD | — |
| Rubber Case Protectors (RCP) | — | — | — | — | — | — | — |  |  | — |  |
| 10-32-UNF-2B (10-32) |  |  |  |  |  |  |  |  |  |  |  |
| Orifice - Brass Press Fit Sintered, 20 Micron (CPO) |  |  |  |  |  |  |  |  |  |  |  |
| Orifice - Brass Press Fit 0.1mm (BP1) |  |  |  |  |  |  |  |  |  |  |  |
| Orifice - Brass Press Fit 0.3mm (BP3) |  |  |  |  |  |  |  |  |  |  |  |
| Orifice - Brass Press Fit 0.8mm (BP8) |  |  |  |  |  |  |  |  |  |  |  |
| Laser Marking (LM) |  |  |  |  |  |  |  |  |  |  |  |
| Stainless Steel Tagging (ST) |  |  |  |  |  |  |  |  |  |  |  |

STANDARD ORIFICE FOR 100 SERIES GAUGE IS 0.3 MM PRESS FIT, UNLESS OTHERWISE SPECIFIED.

* A Steel, Stainless or chrome case & cover ring must be additionally ordered when lenses other than acrylic are utilized on all 100 Series.

** Only 110 Series require a Steel, Stainless or chrome case & cover ring to be additionally ordered when utilizing a set pointer or cover ring. Please consult factory when a set pointer is to be utilized on a 120 Series.

Options & Accessories by Gauge Series

Consult factory for additional non-stock and special accessory availability.

52

200 SERIES LOW PRESSURE DIAPHRAGM GAUGE ACCESSORIES

300 SERIES Brass CASE LIQUID-FILLED GAUGE ACCESSORIES

—    =	Option/accessory is available C    =	Consult factory for availability

STD   =	Standard stock series specification

| MODEL NO. | 25-200 | 25-210 | 25-224 | 40-200 |
| --- | --- | --- | --- | --- |
| CONNECTION |  |  |  |  |
| Stainless Steel Case (SSC) |  |  | — | STD |
| Glass Lens (GL)* |  |  | — | STD |
| Safety Glass Lens (SG)* |  |  | — |  |
| Plexiglass Lens (PL) |  |  | — |  |
| Recalibrator Lens (RL) |  |  | — | — |
| Red Set Pointer (SP) |  |  |  |  |
| Maximum Indicating Pointer (MIP) |  |  |  | C |
| Black Front Flange (BLFF) | — |  | — |  |
| 304SS Front Flange (SSFF) | — | — | — |  |
| Chrome Front Flange (CFF) | — |  | — | — |
| Black Rear Flange (BLRF) |  | — | — | — |
| 304SS Rear Flange (SSRF) | — | — | — |  |
| Black Cover Ring (BCR) |  |  | — | — |
| Stainless Steel Cover Ring (SSCR) |  |  | — | STD |
| Chrome Cover Ring (CCR) |  |  | — | — |
| Black Bezel w/U-Clamp (BBU) | — |  | — | — |
| SS Bezel w/U-Clamp (SSBU) | — |  | — | — |
| Rubber Case Protectors (RCP) |  |  | — |  |
| 10-32-UNF-2B (10-32) |  |  |  |  |
| Orifice - Brass Press Fit 0.3mm (BP3) | — |  |  |  |
| Orifice - Brass Threaded 0.3mm (BT3) |  |  |  |  |
| Laser Marking (LM) |  |  |  |  |
| Stainless Steel Tagging (ST) |  |  |  |  |

STANDARD ORIFICE FOR 200 SERIES GAUGE IS 0.3 MM PRESS FIT, UNLESS OTHERWISE SPECIFIED.

* A Steel, Stainless or chrome cover ring must be additionally ordered when lenses other than acrylic are utilized on all 2-1/2" 200 Series.

Consult factory for additional non-stock and special accessory availability.

—    =	Option/accessory is available

| MODEL NO. | 25-300 | 25-310 | 40-300 | 40-310 |
| --- | --- | --- | --- | --- |
| CONNECTION |  |  |  |  |
| Maximum Indicating Pointer (MIP) |  |  | — | — |
| Polycarbonate Lens (LL) | — | — |  |  |
| Glass Lens Overlay (GLO) |  |  | — | — |
| Safety Glass Overlay (SGO) |  |  | — | — |
| Safety Glass (SG) | — | — |  |  |
| Chrome Front Flange (CFF) |  |  |  |  |
| Chrome Front Flange w/o Holes (CFFN) |  |  |  |  |
| Brass Front Flange (BFF) |  |  |  |  |
| Black Front Flange (BLFF) | — | — |  |  |
| 304SS Rear Flange (SSRF) | — | — |  |  |
| Rear Flange (RF) |  |  | — | — |
| Chrome Cover Ring (CCR) |  |  |  | — |
| Chrome Bezel w/U-Clamp (CBU) | — |  | — |  |
| Adaptor Ring (AR) | — |  | — | — |
| Increased Accuracy from 1.5% to 1.0% (IA) |  |  | — | — |
| Increased Accuracy from 1.0% to 0.5% (IA) | — | — |  |  |
| SAE J1926-3:7/16-20 Adjustable Connection (SST)* |  |  |  |  |
| 10-32-UNF-2B (10-32) |  |  |  |  |
| Orifice - Brass Threaded 0.3mm (BT3) |  |  |  |  |
| Orifice - Brass Threaded 0.4mm (BT4) |  |  |  |  |
| Orifice - Brass Threaded 0.8mm (BT8) |  |  |  |  |
| Rubber Case Protectors (RCP) |  |  |  |  |
| Laser Marking (LM) |  |  |  |  |
| Stainless Steel Tagging (ST) |  |  |  |  |

STANDARD ORIFICE FOR 300 SERIES GAUGE IS 0.8 MM THREADED, UNLESS OTHERWISE SPECIFIED.

- Includes FKM o-ring. Consult factory for availability.

Consult factory for additional non-stock and special accessory availability.

53

400/500 SERIES ALL Stainless Steel PRESSURE GAUGES DRY, LIQUID & AMMONIA GAUGE ACCESSORIES

—    =	Option/accessory is available	C = Consult factory for availability	STD = Standard stock series specification

| MODEL NO. CONNECTION | 15-401 | 15-411 | 25-400 | 25-410 | 40-400 | 40-410 | 60-400 | 60-410 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 25-500 | 25-510 | 40-500 | 40-510 | 60-500 | 60-510 |
| Adjustable Pointer (AP) | — | — | — | — |  |  | STD | STD |
| Safety Glass Lens (SG) | — | — |  |  |  |  | STD | STD |
| Maximum Indicating Pointer (MIP) | — | — |  |  |  |  |  |  |
| Red Set Pointer (SP) | — | — |  |  |  |  |  |  |
| Magnetic Spring Contact, 4" 400 & 410 (MSCS) | — | — | — | — |  |  | — | — |
| 304 SS Front Flange (SSFF) | — | — | — |  |  |  |  |  |
| 304 SS Rear Flange (SSRF) | — | — | C | C |  |  |  |  |
| SS Bezel w/U-Clamp (SSBU) | — | — | — | — | — |  | — |  |
| Flange Ring 304SS (SSFR) | — | — | — |  | — | — | — | — |
| 304SS Panel Mount Clamp (SPMC) | — | — | — |  | — | — | — | — |
| Steel Panel Mount Clamp (PMC) | — | — | — |  | — | — | — | — |
| Increased Accuracy from 1.5% to 1.0% (IA) | — | — |  |  |  |  |  |  |
| Increased Accuracy from 1.0% to 0.5% (IA) | — | — |  |  |  |  |  |  |
| 10-32-UNF-2B (10-32) |  |  |  |  |  |  |  |  |
| Orifice - 316SS Threaded 0.8mm (ST8) |  |  |  |  |  |  |  |  |
| Orifice - 316SS Threaded 0.5mm (ST5) |  |  |  |  |  |  |  |  |
| Rubber Case Protectors (RCP) | — | — |  |  |  | — | — | — |
| Laser Marking (LM) |  |  |  |  |  |  |  |  |
| Stainless Steel Tagging (ST) |  |  |  |  |  |  |  |  |

STANDARD ORIFICE FOR 400/500 SERIES GAUGE IS 0.8 MM THREADED, UNLESS OTHERWISE SPECIFIED.

Consult factory for additional non-stock and special accessory availability.

Options & Accessories by Gauge Series

600/700 SERIES PROCESS GAUGE ACCESSORIES

—    =	Option/accessory is available

| MODEL NO. 45-640 45-740 45-660 45-760 |  |  |  |  |
| --- | --- | --- | --- | --- |
| CONNECTION |  |  |  |  |
| Safety Glass Lens (SG) |  |  |  |  |
| Glass Lens (GL) |  |  |  |  |
| Maximum Indicating Pointer (MIP) |  |  |  |  |
| Overload Stop (OS) |  |  |  |  |
| 10-32-UNF-2B (10-32) |  |  |  |  |
| Orifice - Brass Press Fit 0.3mm (BP3) |  | — |  | — |
| Orifice - Brass Threaded 0.8mm (BT8) |  | — |  | — |
| Orifice - 316SS Threaded 0.8mm (ST8) | — |  | — |  |
| Laser Marking (LM) |  |  |  |  |
| Stainless Steel Tagging (ST) |  |  |  |  |

STANDARD ORIFICE FOR 600/700 SERIES GAUGE IS 0.8 MM THREADED, UNLESS OTHERWISE SPECIFIED.

Consult factory for additional non-stock and special accessory availability.

54

800 SERIES PRECISION TEST GAUGE ACCESSORIES

—    =	Option/accessory is available

| MODEL NO. 60-800 |  |
| --- | --- |
| CONNECTION |  |
| 304 SS Front Flange (SSFF) |  |
| 304 SS Rear Flange (SSRF) |  |
| 10-32-UNF-2B (10-32) |  |
| Orifice - Brass Press Fit 0.3mm (BP3) |  |
| Orifice - Brass Threaded 0.8mm (BT8) |  |
| Laser Marking (LM) |  |
| Stainless Steel Tagging (ST) |  |
| Carrying Case (GC) |  |

STANDARD ORIFICE FOR 800 SERIES GAUGE IS 0.8 MM THREADED, UNLESS OTHERWISE SPECIFIED.

Consult factory for additional non-stock and special accessory availability.

900 SERIES ABS & Stainless Steel LIQUID FILLED PRESSURE GAUGE ACCESSORIES

—    =	Option/accessory is available	C = Consult factory for availability	STD = Standard stock series specification

| MODEL NO. | 15-910 | 25-900 | 25-910 | 25-901 | 25-911 | 40-901 | 40-911 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CONNECTION |  |  |  |  |  |  |  |
| Adjustable Pointer (AP) | — | — | — | — | — |  |  |
| Maximum Indicating Pointer (MIP) | — | — | — |  |  |  |  |
| Red Set Pointer (SP) | — | — | — |  |  |  |  |
| Safety Glass Lens (SG) | — | — | — |  |  |  |  |
| Magnetic Spring Contact Switch 4" 901 & 911 Dry (MSCS) | — | — | — | — | — |  |  |
| Black Front Flange (BLFF) | — | — |  | — | — | — | — |
| 304 SS Front Flange (SSFF) | — | — | — | — |  |  |  |
| 304 SS Rear Flange (SSRF) | — | — | — | — | — |  |  |
| 304 SS Polished Flange Ring (SSFR) | — | — | — | — |  | — | — |
| SS Bezel w/U-Clamp (SSBU) | — | — | — | — | — | — |  |
| 304SS Panel Mount Clamp (SPMC) | — | — | — | — |  | — | — |
| Steel Panel Mount Clamp (PMC) | — | — |  | — |  | — | — |
| Increased Accuracy from 1.5% to 1.0% (IA) | — | — | — |  |  | — | — |
| Increased Accuracy from 1.0% to 0.5% (IA) | — | — | — | — | — |  |  |
| SAE J1926-3:7/16-20 Adjustable Connection (SST)* † | — |  |  |  |  |  |  |
| 1/4" NPT x G1/4 Adaptor (1/4-NPT-MXG1/4-F-BR) |  |  |  |  |  |  |  |
| G1/4 Sealing Washer (G1/4-SEALING-WASHER) |  |  |  |  |  |  |  |
| 10-32-UNF-2B (10-32) |  |  |  |  |  |  |  |
| Orifice - Brass Press Fit 0.3mm (BP3) |  |  |  |  |  |  |  |
| Orifice - Brass Threaded 0.5mm (BT5) |  |  |  |  |  | — | — |
| Orifice - Brass Threaded 0.8mm (BT8) | — | — | — | — | — |  |  |
| Rubber Case Protectors (RCP) | — | — | — |  |  |  |  |
| Dry Out Charge (DRY) | — | — | — |  |  |  |  |
| Laser Marking (LM) |  |  |  |  |  |  |  |
| Stainless Steel Tagging (ST) |  |  |  |  |  |  |  |

STANDARD ORIFICE FOR 900 SERIES GAUGE IS 0.3 MM PRESS FIT, UNLESS OTHERWISE SPECIFIED.

- Includes FKM o-ring. Consult factory for

availability.

** For ranges 60 psi and above.

Consult factory for additional non-stock and special accessory availability.

### GAUGE FILL OPTIONS

| SERIES NO. | VOLUME SILICONE HALOCARBON® -40° SERVICE MINERAL OIL |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 300 SERIES | OZ | D.C. 200 | 4.2 OIL | 86.5 : 13.5 GLYCERIN: H2O (d) | LIGHT VISCOSITY |
| 25-300/25-310 | 2.0 | — | — | — | — |
| 40-300/40-310 | 6.5 | — | — | — | — |
| 500 SERIES |  |  |  |  |  |
| 25-500/25-510 | 2.0 | — | — | — | — |
| 40-500/40-510 | 8.5 | — | — | — | — |
| 60-500/60-510 | 31.0 | — | — | — | — |
| 600/700 SERIES |  |  |  |  |  |
| 45-660/45-760 | 14.0 | — | — | — | — |
| 900 SERIES |  |  |  |  |  |
| 25-900/25-910 | 2.0 | C | C | — | C |
| 25-901/25-911 | 2.0 | C | C | — | C |
| 40-901/40-011 | 8.5 | — | — | — | — |

55

Dial Indicating Gauge Accuracy/Standard Dial  Configuration

Applies to:

300 Series Gauges: 4″	400/500 Series Gauges: 4″ and 6″	900 Series Gauges: 4″

| ACCURACY: ±1.0% full scale |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Primary Scale |  |  | Secondary Scales |  |  |  |  |  |  |  |  |
| Dial Range | Figure | Graduation | kPa | Figure | Graduation | kg/cm2 | Figure | Graduation | bar | Figure | Graduation |
| -30 inHg to 0 psi | -5 inHg | -0.5 inHg | -100 kPa to 0 kPa | -20 kPa | -2 kPa | -1.02 kg/cm2 to 0 kg/cm2 | -0.2 kg/cm2 | -0.02 kg/cm2 | -1 bar to 0 bar | -0.2 bar | -0.02 bar |
| -30 inHg to 15 psi | -10 inHg 5 psi | -1 inHg 0.5 psi | -100 kPa to 100 kPa | -50 kPa 50 kPa | -5 kPa 5 kPa | -1 kg/cm2 to 1.05 kg/cm2 | -0.5 kg/cm2 0.5 kg/cm2 | -0.05 kg/cm2 0.05 kg/cm2 | -1 bar to 1 bar | -0.5 bar 0.5 bar | -0.05 bar 0.05 bar |
| -30 inHg to 30 psi | -10 inHg 5 psi | -1 inHg 0.5 psi | -100 kPa to 205 kPa | -50 kPa 50 kPa | -5 kPa 5 kPa | -1 kg/cm2 to 2.10 kg/cm2 | -1 kg/cm2 0.5 kg/cm2 | -0.1 kg/cm2 0.05 kg/cm2 | -1 bar to 2.05 bar | -0.5 bar 0.5 bar | -0.05 bar 0.05 bar |
| -30 inHg to 60 psi | -30 inHg 10 psi | -2 inHg 1 psi | -100 kPa to 410 kPa | -100 kPa 100 kPa | -10 kPa 10 kPa | -1 kg/cm2 to 4.2 kg/cm2 | -1 kg/cm2 1 kg/cm2 | -0.1 kg/cm2 0.1 kg/cm2 | -1 bar to 4.1 bar | -1 bar 1 bar | .01 bar .1 bar |
| -30 inHg to 100 psi | -30 inHg 20 psi | -5 inHg 2 psi | -100 kPa to 680 kPa | -100 kPa 200 kPa | -20 kPa 20 kPa | -1 kg/cm2 to 7 kg/cm2 | -1 kg/cm2 2 kg/cm2 | -0.2 kg/cm2 0.2 kg/cm2 | -1 bar to 6.8 bar | -1 bar 2 bar | -0.2 bar 0.2 bar |
| -30 inHg to 160 psi | -30 inHg 20 psi | -5 inHg 2 psi | -100 kPa to 1,100 kPa | -100 kPa 200 kPa | -20 kPa 20 kPa | -1 kg/cm2 to 11.2 kg/cm2 | -1 kg/cm2 2 kg/cm2 | -0.2 kg/cm2 0.2 kg/cm2 | -1 bar to 11 bar | -1 bar 2 bar | -0.2 bar 0.2 bar |
| -30 inHg to 200 psi | -30 inHg 40 psi | -5 inHg 4 psi | -100 kPa to 1,360 kPa | -100 kPa 400 kPa | -20 kPa 40 kPa | -1 kg/cm2 to 14 kg/cm2 | -1 kg/cm2 4 kg/cm2 | -0.2 kg/cm2 0.4 kg/cm2 | -1 bar to 13.6 bar | -1 bar 4 bar | -0.2 bar 0.4 bar |
| -30 inHg to 300 psi | -30 inHg 50 psi | -10 inHg 5 psi | -100 kPa to 2,050 kPa | -100 kPa 500 kPa | -50 kPa 50 kPa | -1 kg/cm2 to 21 kg/cm2 | -1 kg/cm2 5 kg/cm2 | -0.5 kg/cm2 0.5 kg/cm2 | -1 bar to 20.5 bar | -1 bar 5 bar | -0.5 bar 0.5 bar |
| 0 psi to 15 psi | 3 psi | 0.2 psi | 0 kPa to 102 kPa | 30 kPa | 2 kPa | 0 kg/cm2 to 1.04 kg/cm2 | 0.3 kg/cm2 | 0.04 kg/cm2 | 0 bar to 1.02 bar | 0.3 bar | 0.02 bar |
| 0 psi to 30 psi | 5 psi | 0.5 psi | 0 kPa to 205 kPa | 50 kPa | 5 kPa | 0 kg/cm2 to 2.1 kg/cm2 | 0.5 kg/cm2 | 0.1 kg/cm2 | 0 bar to 2.05 bar | 0.5 bar | 0.05 bar |
| 0 psi to 60 psi | 10 psi | 1 psi | 0 kPa to 410 kPa | 100 kPa | 10 kPa | 0 kg/cm2 to 4.2 kg/cm2 | 1 kg/cm2 | 0.1 kg/cm2 | 0 bar to 4.1 bar | 1 bar | 0.1 bar |
| 0 psi to 100 psi | 20 psi | 2 psi | 0 kPa to 680 kPa | 200 kPa | 20 kPa | 0 kg/cm2 to 7 kg/cm2 | 2 kg/cm2 | 0.2 kg/cm2 | 0 bar to 6.8 bar | 2 bar | 0.2 bar |
| 0 psi to 160 psi | 20 psi | 2 psi | 0 kPa to 1,100 kPa | 200 kPa | 20 kPa | 0 kg/cm2 to 11.2 kg/cm2 | 2 kg/cm2 | 0.2 kg/cm2 | 0 bar to 11 bar | 2 bar | 0.2 bar |
| 0 psi to 200 psi | 40 psi | 4 psi | 0 kPa to 1,360 kPa | 400 kPa | 40 kPa | 0 kg/cm2 to 14 kg/cm2 | 4 kg/cm2 | 0.4 kg/cm2 | 0 bar to 13.6 bar | 4 bar | 0.4 bar |
| 0 psi to 300 psi | 50 psi | 5 psi | 0 kPa to 2,050 kPa | 500 kPa | 50 kPa | 0 kg/cm2 to 21 kg/cm2 | 5 kg/cm2 | 0.5 kg/cm2 | 0 bar to 20.5 bar | 5 bar | 0.5 bar |
| 0 psi to 400 psi | 50 psi | 5 psi | 0 kPa to 2,750 kPa | 500 kPa | 50 kPa | 0 kg/cm2 to 28 kg/cm2 | 5 kg/cm2 | 0.5 kg/cm2 | 0 bar to 27.5 bar | 5 bar | 0.5 bar |
| 0 psi to 600 psi | 100 psi | 10 psi | 0 kPa to 4,100 kPa | 1,000 kPa | 100 kPa | 0 kg/cm2 to 42 kg/cm2 | 10 kg/cm2 | 1 kg/cm2 | 0 bar to 41 bar | 10 bar | 1 bar |
| 0 psi to 1,000 psi | 200 psi | 20 psi | 0 kPa to 6,800 kPa | 2,000 kPa | 200 kPa | 0 kg/cm2 to 70 kg/cm2 | 20 kg/cm2 | 2 kg/cm2 | 0 bar to 68 bar | 20 bar | 2 bar |
| 0 psi to 1,500 psi | 300 psi | 20 psi | 0 kPa to 10,200 kPa | 3,000 kPa | 200 kPa | 0 kg/cm2 to 104 kg/cm2 | 30 kg/cm2 | 2 kg/cm2 | 0 bar to 102 bar | 30 bar | 2 bar |
| 0 psi to 2,000 psi | 400 psi | 40 psi | 0 kPa to 13,600 kPa | 4,000 kPa | 400 kPa | 0 kg/cm2 to 140 kg/cm2 | 40 kg/cm2 | 4 kg/cm2 | 0 bar to 136 bar | 40 bar | 4 bar |
| 0 psi to 3,000 psi | 500 psi | 50 psi | 0 kPa to 20,500 kPa | 5,000 kPa | 500 kPa | 0 kg/cm2 to 210 kg/cm2 | 50 kg/cm2 | 5 kg/cm2 | 0 bar to 205 bar | 50 bar | 5 bar |
| 0 psi to 5,000 psi | 1,000 psi | 100 psi | 0 kPa to 34,000 kPa | 10,000 kPa | 1,000 kPa | 0 kg/cm2 to 350 kg/cm2 | 100 kg/cm2 | 10 kg/cm2 | 0 bar to 340 bar | 100 bar | 10 bar |
| 0 psi to 6,000 psi | 1,000 psi | 100 psi | 0 kPa to 41,000 kPa | 10,000 kPa | 1,000 kPa | 0 kg/cm2 to 420 kg/cm2 | 100 kg/cm2 | 10 kg/cm2 | 0 bar to 410 bar | 100 bar | 10 bar |
| 0 psi to 7,500 psi | 1,500 psi | 100 psi | 0 kPa to 51,000 kPa | 10,000 kPa | 1,000 kPa | 0 kg/cm2 to 520 kg/cm2 | 100 kg/cm2 | 10 kg/cm2 | 0 bar to 510 bar | 100 bar | 10 bar |
| 0 psi to 10,000 psi | 2,000 psi | 200 psi | 0 kPa to 68,000 kPa | 20,000 kPa | 2,000 kPa | 0 kg/cm2 to 700 kg/cm2 | 200 kg/cm2 | 20 kg/cm2 | 0 bar to 680 bar | 200 bar | 20 bar |
| 0 psi to 15,000 psi | 3,000 psi | 200 psi | 0 kPa to 102,000 kPa | 30,000 kPa | 2,000 kPa | 0 kg/cm2 to 1,040 kg/cm2 | 300 kg/cm2 | 20 kg/cm2 | 0 bar to 1,030 bar | 300 bar | 20 bar |
| 0 psi to 20,000 psi | 4,000 psi | 400 psi | 0 kPa to 136,000 kPa | 40,000 kPa | 4,000 kPa | 0 kg/cm2 to 1,400 kg/cm2 | 400 kg/cm2 | 40 kg/cm2 | 0 bar to 1,360 bar | 400 bar | 40 bar |
| 0 psi to 30,000 psi | 5,000 psi | 500 psi | 0 kPa to 205,000 kPa | 50,000 kPa | 5,000 kPa | 0 kg/cm2 to 2,100 kg/cm2 | 500 kg/cm2 | 50 kg/cm2 | 0 bar to 2,050 bar | 500 bar | 50 bar |
| 0 psi to 40,000 psi | 5,000 psi | 500 psi | 0 kPa to 275,000 kPa | 50,000 kPa | 5,000 kPa | 0 kg/cm2 to 2,800 kg/cm2 | 500 kg/cm2 | 50 kg/cm2 | 0 bar to 2,750 bar | 500 bar | 50 bar |
| 0 psi to 50,000 psi | 10,000 psi | 1000 psi | 0 kPa to 340,000 kPa | 100,000 kPa | 10,000 kPa | 0 kg/cm2 to 3,500 kg/cm2 | 1,000 kg/cm2 | 100 kg/cm2 | 0 bar to 3,400 bar | 1,000 bar | 100 bar |
| 0 psi to 60,000 psi | 10,000 psi | 1000 psi | 0 kPa to 410,000 kPa | 100,000 kPa | 10,000 kPa | 0 kg/cm2 to 4,200 kg/cm2 | 1,000 kg/cm2 | 100 kg/cm2 | 0 bar to 4,100 bar | 1,000 bar | 100 bar |
| 0 psi to 75,000 psi | 15,000 psi | 1000 psi | 0 kPa to 510,000 kPa | 100,000 kPa | 10,000 kPa | 0 kg/cm2 to 5,200 kg/cm2 | 1,000 kg/cm2 | 100 kg/cm2 | 0 bar to 5,100 bar | 1,000 bar | 100 bar |
| 0 psi to 100,000 psi | 20,000 psi | 2000 psi | 0 kPa to 680,000 kPa | 200,000 kPa | 20,000 kPa | 0 kg/cm2 to 7,000 kg/cm2 | 2,000 kg/cm2 | 200 kg/cm2 | 0 bar to 6,800 bar | 2,000 bar | 200 bar |

56

Dial Indicating Gauge Accuracy/Standard Dial  Configuration

Applies to:

200 Series Gauges: 2-1/2″ and 4″	700 Series Gauges (Low Pressure): 4-1/2″

| ACCURACY: ±1.0% full scale |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Standard Dial Configurations |  |  |  |  |  |
| Dial Range | Figure Interval | Graduation Intervals | Dial Range | Figure Interval | Graduation Intervals |
| -15 inH2O to 0 inH2O | -3 inH2O | -0.2 inH2O | 0 oz/in2 to 10 oz/in2 | 2 oz/in2 | 0.2 oz/in2 |
| -30 inH2O to 0 inH2O | -5 inH2O | -0.5 inH2O | 0 oz/in2 to 15 oz/in2 | 3 oz/in2 | 0.2 oz/in2 |
| -60 inH2O to 0 inH2O | -10 inH2O | -1 inH2O | 0 oz/in2 to 30 oz/in2 | 5 oz/in2 | 0.5 oz/in2 |
| -100 inH2O to 0 inH2O | -20 inH2O | -2 inH2O | 0 oz/in2 to 35 oz/in2 | 5 oz/in2 | 0.5 oz/in2 |
| -60 inH2O to 60 inH2O | -10 inH2O ¦ 10 inH2O | -1 inH2O ¦ 1 inH2O | 0 oz/in2 to 60 oz/in2 | 10 oz/in2 | 1 oz/in2 |
| 0 inH2O to 10 inH2O | 2 inH2O | 0.2 inH2O | 0 oz/in2 to 100 oz/in2 | 20 oz/in2 | 2 oz/in2 |
| 0 inH2O to 15 inH2O | 3 inH2O | 0.2 inH2O | 0 oz/in2 to 160 oz/in2** | 40 oz/in2 | 4 oz/in2 |
| 0 inH2O to 30 inH2O | 5 inH2O | 0.5 inH2O | 0 oz/in2 inH2O to 20 oz/in2 inH2O | 4 oz/in2 - 10 inH2O | 0.4 oz/in2 - 1 inH2O |
| 0 inH2O to 60 inH2O | 10 inH2O | 1 inH2O | 0 oz/in2 inH2O to 32 oz/in2 inH2O | 4 oz/in2 - 10 inH2O | 0.5 oz/in2 - 1 inH2O |
| 0 inH2O to 100 inH2O | 20 inH2O | 2 inH2O | 0 psi to 3 psi | 0.5 psi | 0.05 psi |
| * 0 inH2O to 160 inH2O | 40 inH2O | 4 inH2O | 0 psi to 5 psi | 1 psi | 0.1 psi |
| 0 inH2O to 200 inH2O | 40 inH2O | 4 inH2O | 0 psi to 10 psi | 2 psi | 0.2 psi |

* The values in the table are for 2-1/2". On 4" & 4-1/2" 0 inH20 to 160 inH20 gauges, the Figure is 20 inH20, and the Graduation is 2 inH20.

** The values in the table are for 2-1/2". On 4" & 4-1/2" 0 oz/in2 to 160 oz/in2 gauges, the Figure is 20 oz/in2, and the Graduation is 2 oz/in2.

##### 57

Dial Indicating Gauge Accuracy/Standard Dial  Configuration

Applies to:

100 Series Gauges: 4″	300 Series Gauges: 2-1/2″	400/500 Series Gauges: 2-1/2″	900 Series Gauges: 2-1/2″

| ACCURACY: ±1.6% full scale |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Primary Scale |  |  | Secondary Scales |  |  |  |  |  |  |  |  |
| Dial Range | Figure | Graduation | kPa | Figure | Graduation | kg/cm2 | Figure | Graduation | bar | Figure | Graduation |
| -30 inHg to 0 psi | -5 inHg | -0.5 inHg | -100 kPa to 0 kPa | -20 kPa | -2 kPa | -1.02 kg/cm2 to 0 kg/cm2 | -0.2 kg/cm2 | -0.02 kg/cm2 | -1 bar to 0 bar | -0.2 bar | -0.02 bar |
| -30 inHg to 15 psi | -10 inHg 5 psi | -1 inHg 0.5 psi | -100 kPa to 100 kPa | -50 kPa 50 kPa | -5 kPa 5 kPa | -1 kg/cm2 to 1.05 kg/cm2 | -0.5 kg/cm2 0.5 kg/cm2 | -0.05 kg/cm2 0.05 kg/cm2 | -1 bar to 1 bar | -0.5 bar 0.5 bar | -0.05 bar 0.05 bar |
| -30 inHg to 30 psi | -30 inHg 10 psi | -2 inHg 1 psi | -100 kPa to 205 kPa | -100 kPa 100 kPa | -10 kPa 10 kPa | -1 kg/cm2 to 2.10 kg/cm2 | -1 kg/cm2 1 kg/cm2 | -0.1 kg/cm2 0.1 kg/cm2 | -1 bar to 2 bar | -1 bar 1 bar | -0.1 bar 0.1 bar |
| -30 inHg to 60 psi | -30 inHg 20 psi | -5 inHg 2 psi | -100 kPa to 400 kPa | -100 kPa 200 kPa | -20 kPa 20 kPa | -1 kg/cm2 to 4.2 kg/cm2 | -1 kg/cm2 2 kg/cm2 | -2 kg/cm2 0.2 kg/cm2 | -1 bar to 4 bar | -1 bar 2 bar | -0.2 bar 0.2 bar |
| -30 inHg to 100 psi | -30 inHg 20 psi | -5 inHg 2 psi | -100 kPa to 680 kPa | -100 kPa 200 kPa | -20 kPa 20 kPa | -1 kg/cm2 to 7 kg/cm2 | -1 kg/cm2 2 kg/cm2 | -0.2 kg/cm2 0.2 kg/cm2 | -1 bar to 6.8 bar | -1 bar 2 bar | -0.2 bar 0.2 bar |
| -30 inHg to 160 psi | -30 inHg 40 psi | -10 inHg 4 psi | -100 kPa to 1,080 kPa | -100 kPa 400 kPa | -50 kPa 40 kPa | -1 kg/cm2 to 11.2 kg/cm2 | -1 kg/cm2 4 kg/cm2 | -0.5 kg/cm2 0.4 kg/cm2 | -1 bar to 11 bar | -1 bar 4 bar | -0.5 bar 0.4 bar |
| -30 inHg to 200 psi | -30 inHg 40 psi | -10 inHg 4 psi | -100 kPa to 1,360 kPa | -100 kPa 400 kPa | -50 kPa 40 kPa | -1 kg/cm2 to 14 kg/cm2 | -1 kg/cm2 4 kg/cm2 | -0.5 kg/cm2 0.4 kg/cm2 | -1 bar to 13.6 bar | -1 bar 4 bar | -0.5 bar 0.4 bar |
| -30 inHg to 300 psi | -30 inHg 50 psi | -10 inHg 5 psi | -100 kPa to 2,050 kPa | -100 kPa 500 kPa | -50 kPa 50 kPa | -1 kg/cm2 to 21 kg/cm2 | -1 kg/cm2 5 kg/cm2 | -0.5 kg/cm2 0.5 kg/cm2 | -1 bar to 20.5 bar | -1 bar 5 bar | -0.5 bar 0.5 bar |
| 0 psi to 15 psi | 3 psi | 0.2 psi | 0 kPa to 102 kPa | 30 kPa | 2 kPa | 0 kg/cm2 to 1.04 kg/cm2 | 0.3 kg/cm2 | 0.02 kg/cm2 | 0 bar to 1.02 bar | 0.3 bar | 0.02 bar |
| 0 psi to 30 psi | 5 psi | 0.5 psi | 0 kPa to 205 kPa | 50 kPa | 5 kPa | 0 kg/cm2 to 2.1 kg/cm2 | 0.5 kg/cm2 | 0.05 kg/cm2 | 0 bar to 2.05 bar | 0.5 bar | 0.05 bar |
| 0 psi to 60 psi | 10 psi | 1 psi | 0 kPa to 410 kPa | 100 kPa | 10 kPa | 0 kg/cm2 to 4.2 kg/cm2 | 1 kg/cm2 | 0.1 kg/cm2 | 0 bar to 4.10 bar | 1 bar | 0.1 bar |
| 0 psi to 100 psi | 20 psi | 2 psi | 0 kPa to 680 kPa | 200 kPa | 20 kPa | 0 kg/cm2 to 7 kg/cm2 | 2 kg/cm2 | 0.2 kg/cm2 | 0 bar to 6.8 bar | 2 bar | 0.2 bar |
| 0 psi to 160 psi | 40 psi | 4 psi | 0 kPa to 1,080 kPa | 400 kPa | 40 kPa | 0 kg/cm2 to 11.2 kg/cm2 | 4 kg/cm2 | 0.4 kg/cm2 | 0 bar to 11 bar | 4 bar | 0.4 bar |
| 0 psi to 200 psi | 40 psi | 4 psi | 0 kPa to 1,360 kPa | 400 kPa | 40 kPa | 0 kg/cm2 to 14 kg/cm2 | 4 kg/cm2 | 0.4 kg/cm2 | 0 bar to 13.6 bar | 4 bar | 0.4 bar |
| 0 psi to 300 psi | 50 psi | 5 psi | 0 kPa to 2,050 kPa | 500 kPa | 50 kPa | 0 kg/cm2 to 21 kg/cm2 | 5 kg/cm2 | 0.5 kg/cm2 | 0 bar to 20.5 bar | 5 bar | 0.5 bar |
| 0 psi to 400 psi | 100 psi | 10 psi | 0 kPa to 2,700 kPa | 1,000 kPa | 100 kPa | 0 kg/cm2 to 28 kg/cm2 | 10 kg/cm2 | 1 kg/cm2 | 0 bar to 27 bar | 10 bar | 1 bar |
| 0 psi to 600 psi | 100 psi | 10 psi | 0 kPa to 4,100 kPa | 1,000 kPa | 100 kPa | 0 kg/cm2 to 42 kg/cm2 | 10 kg/cm2 | 1 kg/cm2 | 0 bar to 41 bar | 10 bar | 1 bar |
| 0 psi to 1,000 psi | 200 psi | 20 psi | 0 kPa to 6,800 kPa | 2,000 kPa | 200 kPa | 0 kg/cm2 to 70 kg/cm2 | 20 kg/cm2 | 2 kg/cm2 | 0 bar to 68 bar | 20 bar | 2 bar |
| 0 psi to 1,500 psi | 300 psi | 20 psi | 0 kPa to 10,200 kPa | 3,000 kPa | 200 kPa | 0 kg/cm2 to 104 kg/cm2 | 30 kg/cm2 | 2 kg/cm2 | 0 bar to 102 bar | 30 bar | 2 bar |
| 0 psi to 2,000 psi | 400 psi | 40 psi | 0 kPa to 13,600 kPa | 4,000 kPa | 400 kPa | 0 kg/cm2 to 140 kg/cm2 | 40 kg/cm2 | 4 kg/cm2 | 0 bar to 136 bar | 40 bar | 4 bar |
| 0 psi to 3,000 psi | 500 psi | 50 psi | 0 kPa to 20,500 kPa | 5,000 kPa | 500 kPa | 0 kg/cm2 to 210 kg/cm2 | 50 kg/cm2 | 5 kg/cm2 | 0 bar to 205 bar | 50 bar | 5 bar |
| 0 psi to 5,000 psi | 1,000 psi | 100 psi | 0 kPa to 34,000 kPa | 10,000 kPa | 1,000 kPa | 0 kg/cm2 to 350 kg/cm2 | 100 kg/cm2 | 10 kg/cm2 | 0 bar to 340 bar | 100 bar | 10 bar |
| 0 psi to 6,000 psi | 1,000 psi | 100 psi | 0 kPa to 41,000 kPa | 10,000 kPa | 1,000 kPa | 0 kg/cm2 to 420 kg/cm2 | 100 kg/cm2 | 10 kg/cm2 | 0 bar to 410 bar | 100 bar | 10 bar |
| 0 psi to 7,500 psi | 1,500 psi | 100 psi | 0 kPa to 51,000 kPa | 10,000 kPa | 1,000 kPa | 0 kg/cm2 to 520 kg/cm2 | 100 kg/cm2 | 10 kg/cm2 | 0 bar to 510 bar | 100 bar | 10 bar |
| 0 psi to 10,000 psi | 2,000 psi | 200 psi | 0 kPa to 68,000 kPa | 20,000 kPa | 2,000 kPa | 0 kg/cm2 to 700 kg/cm2 | 200 kg/cm2 | 20 kg/cm2 | 0 bar to 680 bar | 200 bar | 20 bar |
| 0 psi to 15,000 psi | 3,000 psi | 200 psi | 0 kPa to 102,000 kPa | 30,000 kPa | 2,000 kPa | 0 kg/cm2 to 1,040 kg/cm2 | 300 kg/cm2 | 20 kg/cm2 | 0 bar to 1,020 bar | 300 bar | 20 bar |

58

Dial Indicating Gauge Accuracy/Standard Dial  Configuration

Applies to:

600/700 Series Gauges: 4-1/2″

| ACCURACY: ±0.5% full scale |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Primary Scale |  |  | Secondary Scales |  |  |  |  |  |  |  |  |
| Dial Range | Figure | Graduation | kPa | Figure | Graduation | kg/cm2 | Figure | Graduation | bar | Figure | Graduation |
| -30 inHg to 0 psi | -5 inHg | -0.2 inHg | -101 kPa to 0 kPa | -20 kPa | -1 kPa | -1.03 kg/cm2 to 0 kg/cm2 | -0.2 kg/cm2 | -0.01 kg/cm2 | -1.01 bar to 0 bar | -0.2 bar | -0.01 bar |
| -30 inHg to 15 psi | -5 inHg 3 psi | -0.5 inHg 0.2 psi | -100 kPa to 102 kPa | -20 kPa 20 kPa | -2 kPa 2 kPa | -1 kg/cm2 to 1.04 kg/cm2 | -0.2 kg/cm2 0.2 kg/cm2 | -0.02 kg/cm2 0.02 kg/cm2 | -1 bar to 1.02 bar | -0.2 bar 0.2 bar | -0.02 bar 0.02 bar |
| -30 inHg to 30 psi | -10 inHg 5 psi | -1 inHg 0.5 psi | -100 kPa to 205 kPa | -50 kPa 50 kPa | -5 kPa 5 kPa | -1 kg/cm2 to 2.10 kg/cm2 | -0.5 kg/cm2 0.5 kg/cm2 | -0.05 kg/cm2 0.05 kg/cm2 | -1 bar to 2.05 bar | -0.5 bar 0.5 bar | -0.05 bar 0.05 bar |
| -30 inHg to 60 psi | -10 inHg 10 psi | -1 inHg 0.4 psi | -100 kPa to 412 kPa | -50 kPa 100 kPa | -5 kPa 4 kPa | -1 kg/cm2 to 4.2 kg/cm2 | -0.5 kg/cm2 1 kg/cm2 | -0.01 kg/cm2 0.04 kg/cm2 | -1 bar to 4.12 bar | -0.5 bar 1 bar | -0.01 bar 0.04 bar |
| -30 inHg to 100 psi | -30 inHg 10 psi | -2 inHg 1 psi | -100 kPa to 680 kPa | -100 kPa 100 kPa | -10 kPa 10 kPa | -1 kg/cm2 to 7 kg/cm2 | -1 kg/cm2 1 kg/cm2 | -0.1 kg/cm2 0.1 kg/cm2 | -1 bar to 6.8 bar | -1 bar 1 bar | -0.1 bar 0.1 bar |
| -30 inHg to 160 psi | -30 inHg 20 psi | -5 inHg 2 psi | -100 kPa to 1,100 kPa | -100 kPa 200 kPa | -20 kPa 20 kPa | -1 kg/cm2 to 11.2 kg/cm2 | -1 kg/cm2 2 kg/cm2 | -0.2 kg/cm2 0.2 kg/cm2 | -1 bar to 11 bar | -1 bar 2 bar | -0.2 bar 0.2 bar |
| -30 inHg to 200 psi | -30 inHg 20 psi | -5 inHg 2 psi | -100 kPa to 1,360 kPa | -100 kPa 200 kPa | -20 kPa 20 kPa | -1 kg/cm2 to 14 kg/cm2 | -1 kg/cm2 2 kg/cm2 | -0.2 kg/cm2 0.2 kg/cm2 | -1 bar to 13.6 bar | -1 bar 2 bar | -0.2 bar 0.2 bar |
| 0 psi to 15 psi | 3 psi | 0.1 psi | 0 kPa to 103 kPa | 30 kPa | 1 kPa | 0 kg/cm2 to 1.05 kg/cm2 | 0.3 kg/cm2 | 0.01 kg/cm2 | 0 bar to 1.03 bar | 0.3 bar | 0.01 bar |
| 0 psi to 30 psi | 5 psi | 0.2 psi | 0 kPa to 206 kPa | 50 kPa | 2 kPa | 0 kg/cm2 to 2.1 kg/cm2 | 0.5 kg/cm2 | 0.02 kg/cm2 | 0 bar to 2.06 bar | 0.5 bar | 0.02 bar |
| 0 psi to 60 psi | 10 psi | 0.4 psi | 0 kPa to 412 kPa | 100 kPa | 4 kPa | 0 kg/cm2 to 4.2 kg/cm2 | 1 kg/cm2 | 0.04 kg/cm2 | 0 bar to 4.12 bar | 1 bar | 0.04 bar |
| 0 psi to 100 psi | 10 psi | 1 psi | 0 kPa to 680 kPa | 100 kPa | 10 kPa | 0 kg/cm2 to 7 kg/cm2 | 1 kg/cm2 | 0.1 kg/cm2 | 0 bar to 6.8 bar | 1 bar | 0.1 bar |
| 0 psi to 160 psi | 20 psi | 1 psi | 0 kPa to 1,100 kPa | 200 kPa | 10 kPa | 0 kg/cm2 to 11.2 kg/cm2 | 2 kg/cm2 | 0.1 kg/cm2 | 0 bar to 11 bar | 2 bar | 0.1 bar |
| 0 psi to 200 psi | 20 psi | 2 psi | 0 kPa to 1,360 kPa | 200 kPa | 20 kPa | 0 kg/cm2 to 14 kg/cm2 | 2 kg/cm2 | 0.2 kg/cm2 | 0 bar to 13.6 bar | 2 bar | 0.2 bar |
| 0 psi to 300 psi | 50 psi | 2 psi | 0 kPa to 2,060 kPa | 500 kPa | 20 kPa | 0 kg/cm2 to 21 kg/cm2 | 5 kg/cm2 | 0.2 kg/cm2 | 0 bar to 20.6 bar | 5 bar | 0.2 bar |
| 0 psi to 400 psi | 40 psi | 4 psi | 0 kPa to 2,720 kPa | 400 kPa | 40 kPa | 0 kg/cm2 to 28 kg/cm2 | 4 kg/cm2 | 0.4 kg/cm2 | 0 bar to 27.2 bar | 4 bar | 0.4 bar |
| 0 psi to 600 psi | 100 psi | 4 psi | 0 kPa to 4,120 kPa | 1,000 kPa | 40 kPa | 0 kg/cm2 to 42 kg/cm2 | 10 kg/cm2 | 0.4 kg/cm2 | 0 bar to 41.2 bar | 10 bar | 0.4 bar |
| 0 psi to 1,000 psi | 100 psi | 10 psi | 0 kPa to 6,800 kPa | 1,000 kPa | 100 kPa | 0 kg/cm2 to 70 kg/cm2 | 10 kg/cm2 | 1 kg/cm2 | 0 bar to 68 bar | 10 bar | 1 bar |
| 0 psi to 1,500 psi | 300 psi | 10 psi | 0 kPa to 10,300 kPa | 3,000 kPa | 100 kPa | 0 kg/cm2 to 105 kg/cm2 | 30 kg/cm2 | 1 kg/cm2 | 0 bar to 103 bar | 30 bar | 1 bar |
| 0 psi to 2,000 psi | 200 psi | 20 psi | 0 kPa to 13,600 kPa | 2,000 kPa | 200 kPa | 0 kg/cm2 to 140 kg/cm2 | 20 kg/cm2 | 2 kg/cm2 | 0 bar to 136 bar | 20 bar | 2 bar |
| 0 psi to 3,000 psi | 500 psi | 20 psi | 0 kPa to 20,600 kPa | 5,000 kPa | 200 kPa | 0 kg/cm2 to 210 kg/cm2 | 50 kg/cm2 | 2 kg/cm2 | 0 bar to 206 bar | 50 bar | 2 bar |
| 0 psi to 5,000 psi | 500 psi | 50 psi | 0 kPa to 34,000 kPa | 5,000 kPa | 500 kPa | 0 kg/cm2 to 350 kg/cm2 | 50 kg/cm2 | 5 kg/cm2 | 0 bar to 340 bar | 50 bar | 5 bar |
| 0 psi to 6,000 psi | 1,000 psi | 40 psi | 0 kPa to 41,200 kPa | 10,000 kPa | 400 kPa | 0 kg/cm2 to 420 kg/cm2 | 100 kg/cm2 | 4 kg/cm2 | 0 bar to 412 bar | 100 bar | 4 bar |
| 0 psi to 10,000 psi | 1,000 psi | 100 psi | 0 kPa to 68,000 kPa | 10,000 kPa | 1,000 kPa | 0 kg/cm2 to 700 kg/cm2 | 100 kg/cm2 | 10 kg/cm2 | 0 bar to 680 bar | 100 bar | 10 bar |
| 0 psi to 15,000 psi | 3,000 psi | 100 psi | 0 kPa to 103,000 kPa | 30,000 kPa | 1,000 kPa | 0 kg/cm2 to 1,050 kg/cm2 | 300 kg/cm2 | 10 kg/cm2 | 0 bar to 1,030 bar | 300 bar | 10 bar |
| 0 psi to 20,000 psi | 2,000 psi | 200 psi | 0 kPa to 136,000 kPa | 20,000 kPa | 2,000 kPa | 0 kg/cm2 to 1,400 kg/cm2 | 200 kg/cm2 | 20 kg/cm2 | 0 bar to 1,360 bar | 200 bar | 20 bar |
| 0 psi to 30,000 psi | 5,000 psi | 200 psi | 0 kPa to 206,000 kPa | 50,000 kPa | 2,000 kPa | 0 kg/cm2 to 2,100 kg/cm2 | 500 kg/cm2 | 20 kg/cm2 | 0 bar to 2,060 bar | 500 bar | 20 bar |
| 0 psi to 40,000 psi | 4,000 psi | 400 psi | 0 kPa to 272,000 kPa | 40,000 kPa | 4,000 kPa | 0 kg/cm2 to 2,800 kg/cm2 | 400 kg/cm2 | 40 kg/cm2 | 0 bar to 2,720 bar | 400 bar | 40 bar |
| 0 psi to 50,000 psi | 5,000 psi | 500 psi | 0 kPa to 340,000 kPa | 50,000 kPa | 5,000 kPa | 0 kg/cm2 to 3,500 kg/cm2 | 500 kg/cm2 | 50 kg/cm2 | 0 bar to 3,400 bar | 500 bar | 50 bar |
| 0 psi to 60,000 psi | 10,000 psi | 400 psi | 0 kPa to 412,000 kPa | 100,000 kPa | 4,000 kPa | 0 kg/cm2 to 4,200 kg/cm2 | 1,000 kg/cm2 | 40 kg/cm2 | 0 bar to 4,120 bar | 1,000 bar | 40 bar |

59

Dial Indicating Gauge Accuracy/Standard Dial  Configuration

Applies to:

100 Series Gauges: 1-1/2″, 2″ and 2-1/2″	400 Series Gauges: 1-1/2″	900 Series Gauges: 1-1/2″ and 2″

| ACCURACY: ±2.5% full scale |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Primary Scale |  |  | Secondary Scales |  |  |  |  |  |  |  |  |
| Dial Range | Figure | Graduation | kPa | Figure | Graduation | kg/cm2 | Figure | Graduation | bar | Figure | Graduation |
| -30 inHg to 0 psi | -5 inHg | -0.5 inHg | -100 kPa to 0 kPa | -20 kPa | -5 kPa | -1 kg/cm2 to 0 kg/cm2 | -0.2 kg/cm2 | -0.05 kg/cm2 | -1 bar to 0 bar | -0.2 bar | -0.05 bar |
| -30 inHg to 15 psi | -10 inHg 5 psi | -1 inHg 0.5 psi | -100 kPa to 100 kPa | -50 kPa 50 kPa | -5 kPa 5 kPa | -1 kg/cm2 to 1.05 kg/cm2 | -0.5 kg/cm2 0.5 kg/cm2 | -0.05 kg/cm2 0.05 kg/cm2 | -1 bar to 1 bar | -0.5 bar 0.5 bar | -0.05 bar 0.05 bar |
| -30 inHg to 30 psi | -30 inHg 10 psi | -2 inHg 1 psi | -100 kPa to 200 kPa | -100 kPa 100 kPa | -10 kPa 10 kPa | -1 kg/cm2 to 2.10 kg/cm2 | -1 kg/cm2 1 kg/cm2 | -0.1 kg/cm2 0.1 kg/cm2 | -1 bar to 2 bar | -1 bar 1 bar | -0.1 bar 0.1 bar |
| -30 inHg to 60 psi | -30 inHg 20 psi | -5 inHg 2 psi | -100 kPa to 400 kPa | -100 kPa 200 kPa | -20 kPa 20 kPa | -1 kg/cm2 to 4.2 kg/cm2 | -1 kg/cm2 2 kg/cm2 | -0.2 kg/cm2 0.2 kg/cm2 | -1 bar to 4 bar | -1 bar 2 bar | -0.2 bar 0.2 bar |
| -30 inHg to 100 psi | -30 inHg 20 psi | -10 inHg 5 psi | -100 kPa to 680 kPa | -100 kPa 200 kPa | -50 kPa 50 kPa | -1 kg/cm2 to 7 kg/cm2 | -1 kg/cm2 2 kg/cm2 | -0.5 kg/cm2 0.5 kg/cm2 | -1 bar to 6.8 bar | -1 bar 2 bar | -0.5 bar 0.5 bar |
| -30 inHg to 160 psi | -30 inHg 40 psi | -10 inHg 4 psi | -100 kPa to 1,100 kPa | -100 kPa 400 kPa | -50 kPa 40 kPa | -1 kg/cm2 to 11.2 kg/cm2 | -1 kg/cm2 4 kg/cm2 | -0.5 kg/cm2 0.4 kg/cm2 | -1 bar to 11 bar | -1 bar 4 bar | -0.5 bar 0.4 bar |
| -30 inHg to 200 psi | -30 inHg 40 psi | -10 inHg 4 psi | -100 kPa to 1,360 kPa | -100 kPa 400 kPa | -50 kPa 40 kPa | -1 kg/cm2 to 14 kg/cm2 | -1 kg/cm2 4 kg/cm2 | -0.5 kg/cm2 0.4 kg/cm2 | -1 bar to 13.6 bar | -1 bar 4 bar | -0.5 bar 0.4 bar |
| -30 inHg to 300 psi | -30 inHg 100 psi | -30 inHg 10 psi | -100 kPa to 2,050 kPa | -100 kPa 1,000 kPa | -100 kPa 100 kPa | -1 kg/cm2 to 21 kg/cm2 | -1 kg/cm2 10 kg/cm2 | -1 kg/cm2 1 kg/cm2 | -1 bar to 20.5 bar | -1 bar 10 bar | -1 bar 1 bar |
| 0 psi to 15 psi | 3 psi | 0.5 psi | 0 kPa to 100 kPa | 30 kPa | 5 kPa | 0 kg/cm2 to 1.05 kg/cm2 | 0.3 kg/cm2 | 0.05 kg/cm2 | - bar to - bar | 0.3 bar | 0.05 bar |
| 0 psi to 30 psi | 5 psi | 0.5 psi | 0 kPa to 205 kPa | 50 kPa | 5 kPa | 0 kg/cm2 to 2.1 kg/cm2 | 0.5 kg/cm2 | 0.05 kg/cm2 | 0 bar to 2.05 bar | 0.5 bar | 0.05 bar |
| 0 psi to 60 psi | 10 psi | 1 psi | 0 kPa to 410 kPa | 100 kPa | 10 kPa | 0 kg/cm2 to 4.2 kg/cm2 | 1 kg/cm2 | 0.1 kg/cm2 | 0 bar to 4.1 bar | 1 bar | 0.1 bar |
| 0 psi to 100 psi | 20 psi | 2 psi | 0 kPa to 680 kPa | 200 kPa | 20 kPa | 0 kg/cm2 to 7 kg/cm2 | 2 kg/cm2 | 0.2 kg/cm2 | 0 bar to 6.8 bar | 2 bar | 0.2 bar |
| 0 psi to 160 psi | 40 psi | 4 psi | 0 kPa to 1,100 kPa | 400 kPa | 40 kPa | 0 kg/cm2 to 11.2 kg/cm2 | 4 kg/cm2 | 0.4 kg/cm2 | 0 bar to 11 bar | 4 bar | 0.4 bar |
| 0 psi to 200 psi | 40 psi | 4 psi | 0 kPa to 1,360 kPa | 400 kPa | 40 kPa | 0 kg/cm2 to 14 kg/cm2 | 4 kg/cm2 | 0.4 kg/cm2 | 0 bar to 13.6 bar | 4 bar | 0.4 bar |
| 0 psi to 300 psi | 50 psi | 5 psi | 0 kPa to 2,050 kPa | 500 kPa | 50 kPa | 0 kg/cm2 to 21 kg/cm2 | 5 kg/cm2 | 0.5 kg/cm2 | 0 bar to 20.5 bar | 5 bar | 0.5 bar |
| 0 psi to 400 psi | 100 psi | 10 psi | 0 kPa to 2,700 kPa | 1,000 kPa | 100 kPa | 0 kg/cm2 to 28 kg/cm2 | 10 kg/cm2 | 1 kg/cm2 | 0 bar to 27 bar | 10 bar | 1 bar |
| 0 psi to 600 psi | 100 psi | 10 psi | 0 kPa to 4,100 kPa | 1,000 kPa | 100 kPa | 0 kg/cm2 to 42 kg/cm2 | 10 kg/cm2 | 1 kg/cm2 | 0 bar to 41 bar | 10 bar | 1 bar |
| 0 psi to 1,000 psi | 200 psi | 20 psi | 0 kPa to 6,800 kPa | 2,000 kPa | 200 kPa | 0 kg/cm2 to 70 kg/cm2 | 20 kg/cm2 | 2 kg/cm2 | 0 bar to 68 bar | 20 bar | 2 bar |
| 0 psi to 1,500 psi | 300 psi | 50 psi | 0 kPa to 10,000 kPa | 3,000 kPa | 500 kPa | 0 kg/cm2 to 105 kg/cm2 | 30 kg/cm2 | 5 kg/cm2 | 0 bar to 100 bar | 30 bar | 5 bar |
| 0 psi to 2,000 psi | 400 psi | 40 psi | 0 kPa to 13,600 kPa | 4,000 kPa | 400 kPa | 0 kg/cm2 to 140 kg/cm2 | 40 kg/cm2 | 4 kg/cm2 | 0 bar to 136 bar | 40 bar | 4 bar |
| 0 psi to 3,000 psi | 500 psi | 50 psi | 0 kPa to 20,500 kPa | 5,000 kPa | 500 kPa | 0 kg/cm2 to 210 kg/cm2 | 50 kg/cm2 | 5 kg/cm2 | 0 bar to 205 bar | 50 bar | 5 bar |
| 0 psi to 5,000 psi | 1000 psi | 100 psi | 0 kPa to 34,000 kPa | 10,000 kPa | 1,000 kPa | 0 kg/cm2 to 350 kg/cm2 | 100 kg/cm2 | 10 kg/cm2 | 0 bar to 340 bar | 100 bar | 10 bar |
| 0 psi to 6,000 psi | 1000 psi | 100 psi | 0 kPa to 41,000 kPa | 10,000 kPa | 1,000 kPa | 0 kg/cm2 to 420 kg/cm2 | 100 kg/cm2 | 10 kg/cm2 | 0 bar to 410 bar | 100 bar | 10 bar |

60

Dial Indicating Gauge Accuracy/Standard Dial  Configuration

Applies to: 800 Series Gauges

| ACCURACY: ±0.25% full scale |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Primary Scale |  |  | Primary Scale |  |  |
| Dial Range | Figure | Graduation | Dial Range | Figure | Graduation |
| 0 psi to 30 psi | 2 psi | 0.1 psi | 0 psi to 1,500 psi | 100 psi | 5 psi |
| 0 psi to 60 psi | 5 psi | 0.2 psi | 0 psi to 2,000 psi | 200 psi | 10 psi |
| 0 psi to 100 psi | 10 psi | 0.5 psi | 0 psi to 3,000 psi | 250 psi | 10 psi |
| 0 psi to 160 psi | 20 psi | 0.8 psi | 0 psi to 5,000 psi | 500 psi | 20 psi |
| 0 psi to 200 psi | 20 psi | 1 psi | 0 psi to 6,000 psi | 500 psi | 20 psi |
| 0 psi to 300 psi | 25 psi | 1 psi |  |  |  |
| 0 psi to 400 psi | 50 psi | 2 psi |  |  |  |
| 0 psi to 600 psi | 50 psi | 2 psi |  |  |  |
| 0 psi to 1,000 psi | 100 psi | 5 psi |  |  |  |

PRESSURE & VACUUM CONVERSIONS

| Pounds per Square Inch | bar | Kilopascals | Kilograms per Square Centimeter | Ounces per Square Inch | Inches of Mercury | Millimeters of Mercury | Inches of Water |
| --- | --- | --- | --- | --- | --- | --- | --- |
| psi | bar | kPa | kg/cm2 | oz-in2 | inHg | mmHg* | inH2O |
| 1 | .0689476 | 6.89476 | .0703069 | 16 | 2.03602 | 51.71485 | 27.6807 |
| 14.5038 | 1 | 100 | 1.019716 | 232.0608 | 29.530 | 750.0626 | 401.8596 |
| .145038 | .01 | 1 | .0101972 | 2.320608 | .295299 | 7.500610 | 401.8596 |
| 14.2233 | .9806649 | 98.06649 | 1 | 227.5739 | 28.95901 | 735.5588 | 393.7118 |
| .0625 | .0043092 | .4309223 | .0043942 | 1 | .1272513 | 3.23218 | 1.73004 |
| .4911542 | .0338639 | 3.386389 | .0345316 | 7.85847 | 1 | 25.4 | 13.59548 |
| .0193368 | .0013332 | .1333225 | .0013595 | .3093888 | .0393701 | 1 | .535255 |
| .0361263 | .0024908 | .2490819 | .0025422 | .578020 | .0735539 | 1.868268 | 1 |

* 1 kPa = 1 kN/m2, 1 mmHg = 1 Torr, 1Kg/cm2 = 1 kp/cm2 (Conversions of: H2O are at 39.2 °F (4 °C): Hg are at 32 °F (0 °C)

Fill Fluid Temperature Table**

CONVERSIONS FOR HYDRAULIC RAM CAPACITY

| psi x AREA = (LBS.) FORCE | TONS = psi x .7854 x D2 | psi = | TONS |
| --- | --- | --- | --- |
|  | 2000 |  | D2 x .0003927 |

| Fill Fluid | Temperature Range (°F) |
| --- | --- |
| Glycerin* | 30 – 300 |
| Silicone 200-10 | -35 – 450 |
| Silicone 710 | 30 – 650 |
| Silicone 550 | -40 – 600 |
| Silicone 510 | -60 – 400 |
| Fluorolube FS-5 | -40 – 500 |
| Silicone 200-350 | 0 – 300 |
| Halocarbon® Oil 6.3 | -40 – 400 |
| Ethylene Glycol | -30 – 300 |
| Propylene Glycol | -50 – 200 |
| Syltherm 800 | -40 – 450 |
| Neobee M-20 | -40 – 320 |

For further assistance with conversions please consult the factory.

- Not recommended for use on vacuum applications

** Temperatures in this table are fluid limits only. Refer to the	61

specific gauge series for gauge temperature limits.

1000 SERIES

##### Rugged, electronic gauge

  - Compound and standard ranges through 0 psig to 10,000 psig

  - 3.31" gauge size

  - Stainless Steel case

  - Stainless Steel wetted parts

  - CE compliant to suppress RFI, EMI and ESD

###### APPLICATIONS

Shown with enhanced software.

SPECIFICATIONS

Pressure ranges	0 psig to 72 psig through 0 psig to 10,000 psig

Compound ranges available

Accuracy	±0.25% full scale (BFSL); ±0.5% terminal point ±1 digit

Temperature ranges	Compensated 32 °F to 140 °F (0 °C to 60 °C)

Effect ±0.15% per 10K at zero and span Span effect is ±0.005% full scale/ °F Media -22 °F to 185 °F (-30 °C to 85 °C)

Ambient 14 °F to 140 °F (-10 °C to 60 °C)

Storage -4 °F to 158 °F (-20 °C to 70 °C)

  - Hydraulics & pneumatics

  - Laboratory & test equipment

  - Leak detection

  - Power generation

  - Water management

Measuring element	Stainless Steel, thin-film measuring element

Connection	1/4" NPT Male, 316 Stainless Steel

Case	Stainless Steel

Bezel	Stainless Steel triangular

Display	Liquid Crystal Display with 0.43" digits

4 digits up to 9999 with bar graph

Power requirement*	2 x 1.5V “AA” battery

4,000 hrs (“AA” 2000 mAh)

Response time	200 ms

Proof pressure	2 times full scale range, maximum 15,000 psi

###### OPTIONAL ENHANCED SOFTWARE FEATURES

Programmable functions Measuring units

Peak memory

Adjustable through front key pad bar, psi, MPa

min/max, display, hold

  - Tare function

  - Password protection

  - Min./max. memory

  - Internal lighting

  - 300° rotatable base

Environmental rating	IP65

Electromagnetic rating	CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Weight	0.88 lb.

* Unregulated

Digital Pressure Gauge

Digital Gauge

Optional Gauge Carrying Case

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

62	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SERIES 1000 |  |  |  |  |  |  |  |  |
| PRESSURE RANGES | 30/72 30/145 72 | -30 inHg to 0 to 72 psig -30 inHg to 0 to 145 psig 0 psig to 72 psig psig = gauge pressure | 145 0 psig to 145 psig 300 0 psig to 300 psig 750 0 psig to 750 psig Other ranges available on request |  | 1450 2300 3625 | 0 psig to 1,450 psig 0 psig to 2,300 psig 0 psig to 3,625 psig | 6000 8500 10000 | 0 psig to 6,000 psig 0 psig to 8,500 psig 0 psig to 10,000 psig * |
| PROCESS CONNECTION 2 1/4″ NPT male |  |  |  |  |  |  |  |  |
| OPTIONS | 1 | Peak memory - standard | GC | Gauge Carrying Case | RCP | Rubber Case Protector |  |  |
|  | 6 | Enhanced software | ST8 | Threaded Orifice |  |  |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

* Standard model will only display 9999 psig.

EXAMPLE	1000 – 1450 – 2 – 1 – GC

Series	1000 Series

Pressure range	0 psig to 1,450 psig

Process connection	1/4" NPT Male

Options	Peak memory

Options	Gauge Carrying Case

1.80"

3.31"

(84 mm)

2.17"

(55 mm)

1.06" NPT

(27 mm)

1/4" NPT

0.51"

(13 mm)

(45.7 mm)

0.18"

(4.6 mm)

1000 SERIES	INFORMATION

ORDERING

DIMENSIONS

3.15" (80 mm)

0.62"

(15.8 mm)

##### 63

###### APPLICATIONS

  - HVAC

  - Hydraulics & pneumatics

  - Injection molding machines

  - Railroad equipment

  - Stamping & forming presses

100 SERIES

##### Vacuum and compound ranges through 0 psig to 15,000 psig

##### Current output

- 316 and 17-4PH Stainless Steel wetted parts

- CE compliant to suppress RFI, EMI and ESD

SPECIFICATIONS

Output signal	4 mA to 20 mA, 2-wire

Pressure ranges	Vacuum through 0 psig to 15,000 psig

Absolute from 0 psia to 15 psia through 0 psia to 300 psia

Accuracy	±0.5% full scale (BFSL); optional ±0.25% full scale (BFSL);

(Includes the effects of non-linearity, hysteresis, non-repeatability, zero point

and full scale errors)

Stability	≤ ±0.2% full scale for 1 year, non-accumulating

Adjustment	≤ ±10% full scale for zero and span

Response time	≤ 1 ms (between 10% and 90% full scale)

Service life	> 100,000,000 load cycles

Temperature ranges	Compensated 32 °F to 176 °F (0 °C to 80 °C)

Effect ±0.017% full scale/ °F for zero and span Media -22 °F to 212 °F (-30 °C to 100 °C)

Ambient -40 °F to 185 °F (-40 °C to 85 °C)

Storage -40 °F to 212 °F (-40 °C to 100 °C)

Power requirement*	10 Vdc to 30 Vdc (4 mA to 20 mA, 2-wire)

Load limitations	≤ (Vpower supply -10)/.020 Amp

Proof pressure	3 times full scale for ranges 0 psi to 5 psi through 0 psi to 200 psi

1.75 times full scale for ranges 0 psi to 300 psi through 0 psi to 10,000 psi

1.5 times full scale for 0 to 15,000 psi

Burst pressure	3.8 times full scale for ranges 0 psi to 5 psi through 0 psi to 200 psi

4 times full scale for ranges 0 psi to 300 psi through 0 psi to 10,000 psi 3 times full scale for 0 psi to 15,000 psi

Measuring element	316 Stainless Steel for vacuum through 300 psi;

17-4PH Stainless Steel for ≥500 psi

Connection	316 Stainless Steel

Housing material	316 Stainless Steel

Environmental rating	IP65

Electromagnetic rating	CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity, over-voltage and short circuit protection

Shock	1000 g’s according to IEC 60068-2-27

Vibration	20 g’s according to IEC 60068-2-6

Weight	Approximately 3.5 oz.

* Unregulated

Industrial Pressure T ransmitters & T ransducers

Current Output

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

64	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| SERIES 100 |  |  |  |  |  |  |
| PRESSURE RANGES | 30vac 30/15 30/30 30/45 30/100 30/150 30/200 30/300 | -30 inHg to 0 psig 5 -30 inHg to 15 psig 10 -30 inHg to 30 psig 15 -30 inHg to 45 psig 25 -30 inHg to 100 psig 30 -30 inHg to 150 psig 60 -30 inHg to 200 psig 100 -30 inHg to 300 psig 150 | 0 psig to 5 psig 0 psig to 10 psig 0 psig to 15 psig 0 psig to 25 psig 0 psig to 30 psig 0 psig to 60 psig 0 psig to 100 psig 0 psig to 150 psig psig = gauge pressure | 200 0 psig to 200 psig 3000 0 psig to 3,000 psig 300 0 psig to 300 psig 4000 0 psig to 4,000 psig 500 0 psig to 500 psig 5000 0 psig to 5,000 psig 600 0 psig to 600 psig 6000 0 psig to 6,000 psig 750 0 psig to 750 psig 7500 0 psig to 7,500 psig 1000 0 psig to 1,000 psig 10000 0 psig to 10,000 psig 1500 0 psig to 1,500 psig 15000 0 psig to 15,000 psig 2000 0 psig to 2,000 psig psia = absolute pressure Other ranges available on request | 15A 30A 60A 100A 150A 200A 300A | 0 psia to 15 psia 0 psia to 30 psia 0 psia to 60 psia 0 psia to 100 psia 0 psia to 150 psia 0 psia to 200 psia 0 psia to 300 psia |
| ACCURACIES | 1 | ±0.5% full scale (BFSL) |  | 2 ±0.25% full scale (BFSL) |  |  |
| OUTPUT SIGNAL | 1 | 4 mA to 20 mA, 2-wire |  |  |  |  |
| PROCESS 1 1/8″ NPT male 3 SAE J1926-3:7/16-20 Adjustable 9 SAE J1926-1:7/16-20 CONNECTIONS 2 1/4″ NPT male 4 1/8″ NPT female 10 G1/4 male |  |  |  |  |  |  |
| ELECTRICAL CONNECTIONS | 1 2 3 | 36″ cable (connected to option 7) 4-pin Bendix 6-pin Bendix |  | - 1/2″ NPT conduit ( with 36″ cable) - Mini-Hirschmann (DIN EN 175301-803 Form C) | 25 36 | M12 x 1 (4-pin) Integral cable 36″ |
| OPTION | ST8 | Threaded Orifice |  |  |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

EXAMPLE

Series	100 Series

Pressure range	0 psig to 500 psig

Accuracy	±0.5% full scale (BFSL)

Output signal	4 mA to 20 mA, 2-wire

Process connection	1/4" NPT Male

Electrical connection	Mini-Hirschmann

Option	Threaded Orifice

100 – 500 – 1 – 1 – 2 – 7 – ST8

| Load Limitations 4 mA to 20 mA output |  |  |
| --- | --- | --- |
| Vmin | = | 10V + (.020 x RL) |
| RL | = | Loop resistance (Ω) RL = RS + RW |
| RS | = | Sensor resistance (Ω) |
| RW |  | Wire resistance (Ω) |

1.38"

(35 mm)

  - " sq

(15.8 mm)

1.61"

(41 mm)

0.71"

(18.1 mm)

0.72"

(18.2 mm)

0.72"

(18.2 mm)

1.28"

(32.5 mm)

1/2" NPT conduit with 36" jacketed cable

* 6 pin Bendix	* 4 pin Bendix	* M12 x 1 (4-pin)

2.30"

(58.5 mm)

| WIRING |  |  |  |  |
| --- | --- | --- | --- | --- |
| Wire | Bendix 4-pin or 6-pin | Mini- Hirschmann | Cable | M12 x 1 |
| + Supply | pin A | pin 1 | Red | pin 1 |
| + Output | pin B | pin 2 | Black | pin 3 |

* Note: Mate supplied separately or customer supplied.

  - " HEX

(17 mm)

14" NPT

1.06"

(27 mm)

Mini-Hirschmann

0.51"

(13 mm)

100 SERIES	INFORMATION

ORDERING

DIMENSIONS

##### 65

200

SERIES

    - Ranges from vacuum to 0 psig to 15,000 psig; absolute ranges from 0 psia to 15 psia through 0 psia to 300 psia

##### Voltage output

    - 316 and 17-4PH Stainless Steel wetted parts

    - CE compliant to suppress RFI, EMI and ESD

###### APPLICATIONS

    - HVAC

    - Hydraulics & pneumatics

    - Injection molding machines

    - Railroad equipment

    - Stamping & forming presses

SPECIFICATIONS

Output signals	0 Vdc to 5 Vdc, 3-wire; 0 Vdc to 10 Vdc, 3-wire; 1 Vdc to 5 Vdc, 3-wire; 1 Vdc to 6 Vdc, 3-wire; 1 Vdc to 11 Vdc, 3-wire

Pressure ranges	Vacuum through 0 psig to 15,000 psig

Absolute from 0 psia to 15 psia through 0 psia to 300 psia

Accuracy	±0.5% full scale (BFSL); optional ±0.25% full scale (BFSL);

(Includes the effects of non-linearity, hysteresis, non-repeatability, zero point and

full scale errors)

Stability	≤ ±0.2% full scale per year, non-accumulating

Adjustment	±10% full scale for zero and span Response time	≤ 1 ms (between 10% and 90% full scale) Service life	> 100,000,000 load cycles

Temperature ranges	Compensated 32 °F to 176 °F (0 °C to 80 °C)

Effect ±0.017% full scale/ °F for zero and span Media -22 °F to 212 °F (-30 °C to 100 °C)

Ambient -40 °F to 185 °F (-40 °C to 85 °C)

Storage -40 °F to 212 °F (-40 °C to 100 °C)

Power requirement*	10 Vdc to 30 Vdc (0 Vdc to 5 Vdc, 3-wire, 1 Vdc to 5 Vdc, 3-wire,

- Vdc to 6 Vdc, 3-wire)

14 Vdc to 30 Vdc (0 Vdc to 10 Vdc, 3-wire, 1 Vdc to 11 Vdc, 3-wire)

Load limitations	≥ 5,000 Ω for 0 Vdc to 5 Vdc, 1 Vdc to 5 Vdc, and 1 Vdc to 6 Vdc outputs;

≥10,000 Ω for 0 Vdc to 10 Vdc and 1 Vdc to 11 Vdc outputs. Current consumption 8 mA

Proof pressure	3 times full scale for ranges 0 psi to 5 psi through 0 psi to 200 psi

1.75 times full scale for ranges 0 psi to 300 psi through 0 psi to 10,000 psi

1.5 times full scale for 0 psi to 15,000 psi

Burst pressure	3.8 times full scale for ranges 0 psi to 5 psi through 0 psi to 200 psi

4 times full scale for ranges 0 psi to 300 psi through 0 psi to 10,000 psi 3 times full scale for 0 psi to 15,000 psi

Measuring element	316 Stainless Steel for vacuum through 300 psi;

17-4PH Stainless Steel for ≥500 psi

Connection	316 Stainless Steel

Housing material	316 Stainless Steel

Environmental rating	IP65

Electromagnetic rating CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity, over-voltage and short circuit protection

Shock	1,000 g’s according to IEC 60068-2-27

Vibration	20 g’s according to IEC 60068-2-6

Weight	Approximately 3.5 oz.

Industrial Pressure T ransmitters & T ransducers

Voltage Output

* Unregulated

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

66	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SERIES 200 |  |  |  |  |  |  |  |
| PRESSURE | 30vac | -30 inHg to 0 psig | 30/300 | -30 inHg to 300 psig | 200 0 psig to 200 psig 3000 0 psig to 3,000 psig | 15A | 0 psia to 15 psia |
| RANGES | 30/15 | -30 inHg to 15 psig | 5 | 0 psig to 5 psig | 300 0 psig to 300 psig 4000 0 psig to 4,000 psig | 30A | 0 psia to 30 psia |
|  | 30/30 | -30 inHg to 30 psig | 10 | 0 psig to 10 psig | 500 0 psig to 500 psig 5000 0 psig to 5,000 psig | 60A | 0 psia to 60 psia |
|  | 30/45 | -30 inHg to 45 psig | 15 | 0 psig to 15 psig | 600 0 psig to 600 psig 6000 0 psig to 6,000 psig | 100A | 0 psia to 100 psia |
|  | 30/60 | -30 inHg to 60 psig | 30 | 0 psig to 30 psig | 750 0 psig to 750 psig 7500 0 psig to 7,500 psig | 150A | 0 psia to 150 psia |
|  | 30/100 | -30 inHg to 100 psig | 60 | 0 psig to 60 psig | 1000 0 psig to 1,000 psig 10000 0 psig to 10,000 psig | 200A | 0 psia to 200 psia |
|  | 30/150 | -30 inHg to 150 psig | 100 | 0 psig to 100 psig | 1500 0 psig to 1,500 psig 15000 0 psig to 15,000 psig | 300A | 0 psia to 300 psia |
|  | 30/200 | -30 inHg to 200 psig | 150 | 0 psig to 150 psig | 2000 0 psig to 2,000 psig |  |  |
|  |  |  |  | psig = gauge pressure | psia = absolute pressure Other ranges available on request |  |  |
| ACCURACIES | 1 | ±0.5% full scale (BFSL) |  | 2 ±0.25% full scale (BFSL) |  |  |  |
| OUTPUT SIGNALS | 2 | 0 Vdc to 5 Vdc, 3-wire | 3 | 1 Vdc to 5 Vdc, 3-wire | 4 1 Vdc to 6 Vdc, 3-wire 5 0 Vdc to 10 Vdc, 3-wire | 6 | 1 Vdc to 11 Vdc, 3-wire |
| PROCESS | 1 | 1/8″ NPT male | 3 | SAE J1926-3:7/16-20 adjustable 9 SAE J1926-1:7/16-20 |  |  |  |
| CONNECTIONS | 2 | 1/4″ NPT male | 4 | 1/8″ NPT female 10 G1/4 male |  |  |  |
| ELECTRICAL CONNECTION | 1 2 3 | 36″ cable (connected to option 7) 6 1/2″ NPT conduit ( with 36″ cable) 25 4-pin Bendix 7 Mini-Hirschmann (DIN EN 175301-803 form C) 36 6-pin Bendix NOTE: 0 Vdc to 5 Vdc and 0 Vdc to 10 Vdc outputs are also available in 4-wire configurations for use with other electrical systems. |  |  |  |  | M12 x 1 (4-pin) Integral cable 36" |
| OPTION | ST8 | Threaded Orifice |  |  |  |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

EXAMPLE	200 – 500 – 1 – 2 – 2 – 7 – ST8

Series	200 Series

Pressure range	0 psig to 500 psig

Accuracy	±0.5% full scale (BFSL)

Output signal	0 Vdc to 5 Vdc, 3-wire

Process connection	1/4" NPT Male

Electrical connection	Mini-Hirschmann

Option	Threaded Orifice

1.38"

(35 mm)

  - " sq.

(15.8 mm)

1.61"

(41 mm)

0.71"

(18.1 mm)

0.72"

(18.2 mm)

0.72"

(18.2 mm)

1.28"

(32.5 mm)

1/2" NPT Conduit with 36" jacketed cable

* 6 pin Bendix	* 4 pin Bendix	* M12 x 1 (4-pin)

2.30"

(58.5 mm)

| WIRING |  |  |  |  |
| --- | --- | --- | --- | --- |
| Wire | Bendix 4-pin or 6-pin | Mini- Hirschmann | Cable | M12 x 1 |
| + Supply | pin A | pin 1 | Red | pin 1 |
| Common | pin B | pin 2 | Black | pin 3 |
| + Output | pin C | pin 3 | White | pin 4 |

* Note: mate supplied separately or customer supplied

0.69" HEX

(17 mm) 1/4" NPT

1.06"

(27 mm)

Mini-Hirschmann

0.51"

(13 mm)

200 SERIES	INFORMATION

ORDERING

DIMENSIONS

##### 67

###### APPLICATIONS

    - Irrigation

    - Tank monitoring

    - Water & wastewater

    - Well head measurement

612 SERIES

##### Ranges from 0 inH2O to 50 inH2O through 0 psig to 1,000 psig

- Current and voltage outputs available

- 316 Stainless Steel, polyamide and polyurethane wetted parts

- CE compliant to suppress RFI, EMI and ESD

SPECIFICATIONS

Output signals	4 mA to 20 mA, 2-wire; 0 Vdc to 5 Vdc and 0 Vdc to 10 Vdc, 3-wire;

0.5 Vdc to 2.5 Vdc, 3-wire

Pressure ranges	0 inH2O to 50 inH2O through 0 psig to 1,000 psig

Accuracy	± 0.25% full scale (BFSL); optional ± 0.125% full scale (BFSL);

(includes the effects of non-linearity, hysteresis, non-repeatability, zero point and full scale errors)

Stability	≤ ± 0.2% full scale for 1 year, non-accumulating

Response time	≤ 1 ms (between 10% and 90% full scale)

Service life	> 100,000,000 load cycles

Temperature ranges	Compensated 32 °F to 122 °F/0 °C to 50 °C

Effect ± 0.01%/ °F for zero and span Media 14 °F to 122 °F / -10 °C to 50 °C Storage -22 °F to 175 °F/-30 °C to 80 °C

Power requirement*	10 Vdc to 30 Vdc (4 mA to 20 mA, 2-wire, 0 Vdc to 5 Vdc, 3-wire)

5 Vdc to 30 Vdc (0.5 Vdc to 2.5 Vdc, 3-wire)

14 Vdc to 30 Vdc (0 Vdc to 10 Vdc, 3-wire)

Load limitations	≤ (VPower-10)/0.020 Amp for 4 mA to 20 mA

≥ 10,000 Ω for 0 Vdc to 10 Vdc, 3-wire

≥ 5,000 Ω for 0 Vdc to 5 Vdc, 3-wire

Proof pressure	2 times range

Burst pressure	4 times range

Measuring element	Cap: Polyamide, 316 Stainless Steel with weighted nosecone

Cable: Polyurethane, optional FEP or PVC with double water block

Connection	316 Stainless Steel

Housing material	316 Stainless Steel

Environmental rating	IP68

Electromagnetic rating	CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity protection, short circuit and optional lightning protection per EN 6100-4-5; 1.5J

Shock	100 g’s according to IEC 60068-2-27

Vibration	15 g’s according to IEC 60068-2-6

Weight	Approximately 7 oz. with standard nosecone - cable extra

Industrial Level T ransmitters & T ransducers

Submersible

* Unregulated

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

68	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| SERIES 612 |  |  |  |  |  |  |
| PRESSURE RANGES | 50 inH2O 0 inH2O to 50 inH2O 2 0 psig to 2 psig (4.6 ftH2O) 100 inH2O 0 inH2O to 100 inH2O 3 0 psig to 3 psig (6.9 ftH2O) 150 inH2O 0 inH2O to 150 inH2O 5 0 psig to 5 psig (11.5 ftH2O) 200 inH2O 0 inH2O to 200 inH2O 10 0 psig to 10 psig (23.1 ftH2O) 400 inH2O 0 inH2O to 400 inH2O 15 0 psig to 15 psig (34.6 ftH2O) psig = gauge pressure Other ranges available on request |  | 20 25 | 0 psig to 20 psig (46.2 ftH2O) 0 psig to 25 psig (57.7 ftH2O) | 200 300 | 0 psig to 200 psig (461.3 ftH2O) 0 psig to 300 psig (692.5 ftH2O) 0 psig to 350 psig (807.9 ftH2O) 0 psig to 500 psig (1154.2 ftH2O) 0 psig to 750 psig (1733.3 ftH2O) 0 psig to 1,000 psig (2311.0 ftH2O) |
|  |  |  | 30 | 0 psig to 30 psig (69.2 ftH2O) | 350 |  |
|  |  |  | 60 | 0 psig to 60 psig (138.5 ftH2O) | 500 |  |
|  |  |  | 100 | 0 psig to 100 psig (230.8 ftH2O) | 750 |  |
|  |  |  | 150 | 0 psig to 150 psig (346.3 ftH2O) | 1000 |  |
| ACCURACIES | 1 | ±0.25% full scale (BFSL) | 2 | ±0.125% full scale (BFSL) |  |  |
| OUTPUT SIGNALS | 1 | 4 mA to 20 mA, 2-wire | 5 | 0 Vdc to 10 Vdc, 3-wire |  |  |
|  | 2 | 0 Vdc to 5 Vdc, 3-wire | 11 | 0.5 Vdc to 2.5 Vdc, 3-wire |  |  |
| PROCESS CONNECTIONS | N T | Nosecone G 1/2 B x 1/2″ NPT male with 1/4″ NPT female | W | Nosecone w/added weight (1.1 lb.) |  |  |
| ELECTRICAL CONNECTIONS | XX 22-XX | Standard polyurethane (PUR) cable Optional water-blocked PVC cable (200+ psi only) NOTE: XX = length of cable in feet. | 38-XX | Optional FEP cable |  |  |
| OPTIONS | PT1 DC | PT100 RTD * CBC Cable Clamp Desiccant Cartridge LP Lightning Protection * | FE JB | Filter Element Cable Junction Box |  |  |

* Not available for PVC cable

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

EXAMPLE	612 – 5 – 1 – 1 – N – 50

Series	612 Series

Pressure range	0 psig to 5 psig

Accuracy	±0.25% full scale (BFSL)

Output signal	4 mA to 20 mA, 2-wire

Process connection	Nosecone

Electrical connection	50' of submersible polyurethane cable

1.06″

(27 mm)

  - ″ Dia (5 mm)

G1/2

Weighted nosecone	NPT adapter

1.06″

(27 mm)

FKM o-ring 1.06″ HEX

(27 mm)

3.90″

(99 mm)

5.12″ (130 mm)

1.81″

(46 mm)

0.73″ (18.5 mm)

0.20″

(5 mm)

1/2″ NPT

Male	1/4″ NPT

Female

612 SERIES	INFORMATION

ORDERING

DIMENSIONS

| Wiring | Cable |
| --- | --- |
| + Supply | Red |
| + Output | Black |

| Wiring | Cable |
| --- | --- |
| + Supply | Red |
| Common | Black |
| + Output | White |

WIRE WIRING	3-WIRE WIRING

69

Industrial Level T ransmitters & T ransducers

Cage-Protected Submersible

613 SERIES

##### Ranges from 0 psi to 5 psi through 0 psi to 300 psi

      - Current & voltage outputs available

      - 316 Stainless Steel and polyurethane wetted parts

      - CE compliant to suppress RFI, EMI and ESD

###### APPLICATIONS

  - Lift stations

  - Sewage

  - Slurry tanks

  - Storm canals

  - Water & wastewater

  - Wet wells

SPECIFICATIONS

Output signals	4 mA to 20 mA, 2-wire; 0 Vdc to 5 Vdc and 0 Vdc to 10 Vdc, 3-wire;

0.5 Vdc to 2.5 Vdc, 3-wire

Pressure ranges	0 psi to 5 psi through 0 psi to 300 psi

Accuracy	± 0.25% full scale (BFSL); optional ± 0.125% full scale (BFSL);

(includes the effects of non-linearity, hysteresis, non-repeatability, zero point and full scale errors)

Stability	≤ ± 0.2% full scale for 1 year, non-accumulating

Response time	≤ 1 ms (between 10% and 90% full scale)

Service life	> 100,000,000 full scale cycles

Temperature measurement Optional PT100, 4-wire per IEC 60751

Temperature ranges	Compensated 32 °F to 122 °F/0 °C to 50 °C

Effect ± 0.01%/ °F for zero and span Media 14 °F to 122 °F / -10 °C to 50 °C

Storage -22 °F to 175 °F/ -30 °C to 80 °C

Power requirement*	10 Vdc to 30 Vdc (4 mA to 20 mA, 2-wire, 0 Vdc to 5 Vdc, 3-wire)

5 Vdc to 30 Vdc (0.5 Vdc to 2.5 Vdc, 3-wire)

14 Vdc to 30 Vdc (0 Vdc to 10 Vdc, 3-wire)

Load limitations	≤ (VPower-10)/0.020 Amp for 4 mA to 20 mA

≥ 10,000 Ω for 0 Vdc to 10 Vdc, 3-wire

≥ 5,000 Ω for 0 Vdc to 5 Vdc, 3-wire

Proof pressure	2 times range

Burst pressure	4 times range

Measuring element	Cage seal: All 316 Stainless Steel

Cable: Polyurethane, optional FEP

Connection	316 Stainless Steel

Housing material	316 Stainless Steel

Environmental rating	IP68

Electromagnetic rating	CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity protection, short circuit and optional lightning protection per EN 6100-4-5; 1.5J

Shock	100 g’s according to IEC 60068-2-27

Vibration	15 g’s according to IEC 60068-2-6

Weight	Approximately 3.2 lb. - cable extra

* Unregulated

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

70	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SERIES 613 |  |  |  |  |  |  |  |  |
| PRESSURE RANGES | 5 10 15 | 0 psi to 5 psi (11.55 ft/H2O) 0 psi to 10 psi (23.10 ft/H2O) 0 psi to 15 psi (34.65 ft/H2O) | 20 30 50 | 0 psi to 20 psi (46.20 ft/H2O) 0 psi to 30 psi (69.30 ft/H2O) 0 psi to 50 psi (115.50 ft/H2O) | 75 100 150 | 0 psi to 75 psi (173.25 ft/H2O) 0 psi to 100 psi (231.00 ft/H2O) 0 psi to 150 psi (346.50 ft/H2O) | 300 | 0 psi to 300 psi (693 ft/H2O) |
| ACCURACIES | 1 | ±0.25% full scale (BFSL) |  |  | 2 | ±0.125% full scale (BFSL) |  |  |
| OUTPUT SIGNALS | 1 2 | 4 mA to 20 mA, 2-wire 0 Vdc to 5 Vdc, 3-wire |  |  | 5 11 | 0 Vdc to 10 Vdc, 3-wire 0.5 Vdc to 2.5 Vdc, 3-wire |  |  |
| ELECTRICAL CONNECTIONS | XX | Standard polyurethane (PUR) cable NOTE: XX = length of cable in feet. |  |  | 38-XX | Optional FEP cable |  |  |
| OPTIONS | CBC DC | Cable Clamp Desiccant Cartridge | FE JB | Filter Element Cable Junction Box | LP LR | Lightning Protection * Lifting Ring | PT1 | PT100 RTD * |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

- Only available with PUR cable

EXAMPLE	613 – 5 – 1 – 1 – 50' – LR

Series	613 Series

Pressure range	psi to 5 psi

Accuracy	±0.25% full scale (BFSL)

Output signal	4 mA to 20 mA, 2-wire

Electrical connection	50' of submersible polyurethane cable

Option	Lifting Ring

Optional Cable Clamp

1/2″ NPT

Ø 1.06″

(27 mm)

4.44″ (113 mm)

1.75″	1.25″

(44 mm) (32 mm) (27 mm)

1.06″

0.25″

(6 mm)

2.14″

(54 mm) Active area

Ø 3.75″

(95 mm)

Optional Cable Junction Box

Optional Desiccant Cartridge

Optional Filter Element

Optional Lifting Ring

613 SERIES	INFORMATION

ORDERING

DIMENSIONS

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

71

615/616 SERIES

##### Vacuum ranges through 0 psig to 145,000 psig; absolute ranges from 0 psia to 15 psia through 0 psia to 300 psia

  - Current and voltage outputs available

  - 316 and 17-4PH Stainless Steel wetted parts

  - CE compliant to suppress RFI, EMI and ESD

###### APPLICATIONS

  - Construction

  - Hydraulics & pneumatics

  - Laboratory & test equipment

  - Power generation

  - Stamping & forming presses

  - Transportation

Also available with our 1800 Series

Attachable Loop Indicator.

Visit www.noshok.com for more

High pressure model

SPECIFICATIONS

Output signals	4 mA to 20 mA, 2-wire;

0 Vdc to 5 Vdc, 0 Vdc to 10 Vdc, 1 Vdc to 5 Vdc,3-wire

Pressure ranges	Vacuum through 0 psig to 145,000 psig

Absolute from 0 psia to 15 psia through 0 psia to 300 psia

Accuracy	± 0.25% full scale (BFSL); optional ± 0.125% full scale (BFSL); (includes the effects of non-linearity, hysteresis, non-repeatability, zero point and full scale errors)

Stability	≤ ±0.2% full scale for 1 year, non-accumulating

Adjustment	± 10% full scale for zero and span

Response time	Less than 1 ms (between 10% and 90% full scale)

Service life	>100,000,000 load cycles

Temperature ranges	Compensated 32 °F to 175 °F (0 °C to 80 °C)

Effect ± 0.01%/ °F for zero and span Media -20 °F to 212 °F (-30 °C to 100 °C)

Ambient -15 °F to 175 °F (-10 °C to 80 °C)

Storage -40 °F to 212 °F (-40 °C to 100 °C)

Power requirement*	10 Vdc to 30 Vdc (4 mA to 20 mA, 2-wire, 1 Vdc to 5 Vdc, 3-wire, 1 Vdc to 6 Vdc, 3-wire, 0 Vdc to 5 Vdc, 3-wire)

14 Vdc to 30 Vdc (0 Vdc to 10 Vdc, 3-wire, 1 Vdc to 11 Vdc, 3-wire)

Load limitations	≤ (VPower-10)/0.020 Amp for 4 mA to 20 mA

≥ 10,000 Ω for 0 Vdc to 10 Vdc, 3-wire

≥ 5,000 Ω for 0 Vdc to 5 Vdc, 3-wire

Proof pressure	3 times full scale for ranges 0 psi to 2 psi through 0 psi to 200 psi

1.75 times full scale for ranges 0 psi to 300 psi through 0 psi to 10,000 psi

1.5 times full scale for 0 psi to 15,000 psi

1.2 times full scale for ranges 0 psi to 20,000 psi through 0 psi to 145,000 psi

Burst pressure	3.8 times full scale for ranges 0 psi to 2 psi through 0 psi to 200 psi

4 times full scale for ranges 0 psi to 300 psi through 0 psi to 10,000 psi 3 times full scale for 0 psi to 15,000 psi

1.5 times full scale for ranges 0 psi to 20,000 psi through 0 psi to 145,000 psi

Measuring element	316 Stainless Steel for vacuum through 300 psi;

17-4PH Stainless Steel for ≥500 psi

Connection	316 Stainless Steel

Housing material	316 Stainless Steel

Environmental rating	IP65

Electromagnetic rating	CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity, overvoltage and short circuit protection

Shock	1,000 g’s according to IEC 60068-2-27

Vibration	15 g’s according to IEC 60068-2-6

Weight	Approximately 7.2 oz.

Industrial Pressure T ransmitters & T ransducers

High Accuracy Heavy-Duty

information.	* Unregulated

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

72	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |
| --- | --- | --- | --- |
| SERIES | 615 | (Internal diaphragm) 616 | (Front flush diaphragm) |
| PRESSURE | 30vac | -30 inHg to 0 psig 2 0 psig to 2 psig 150 -30 inHg to 15 psig 3 0 psig to 3 psig 200 -30 inHg to 30 psig 5 0 psig to 5 psig 300 -30 inHg to 60 psig 10 0 psig to 10 psig 500 -30 inHg to 100 psig 15 0 psig to 15 psig 600 -30 inHg to 150 psig 30 0 psig to 30 psig 750 -30 inHg to 200 psig 60 0 psig to 60 psig 1000 -30 inHg to 300 psig 100 0 psig to 100 psig 1500 psig = gauge pressure psia = absolute pressure | 0 psig to 150 psig 2000 0 psig to 2,000 psig 20000 0 psig to 20,000 psig * 145000 0 psig to 145,000 psig |
| RANGES | 30/15 |  | 0 psig to 200 psig 3000 0 psig to 3,000 psig 30000 0 psig to 30,000 psig 15A 0 psia to 15 psia |
|  | 30/30 |  | 0 psig to 300 psig 4000 0 psig to 4,000 psig 36000 0 psig to 36,000 psig 30A 0 psia to 30 psia |
|  | 30/60 |  | 0 psig to 500 psig 5000 0 psig to 5,000 psig 58000 0 psig to 58,000 psig 60A 0 psia to 60 psia |
|  | 30/100 |  | 0 psig to 600 psig 6000 0 psig to 6,000 psig 72000 0 psig to 72,000 psig 100A 0 psia to 100 psia |
|  | 30/150 |  | 0 psig to 750 psig 7500 0 psig to 7,500 psig 87000 0 psig to 87,000 psig 150A 0 psia to 150 psia |
|  | 30/200 |  | 0 psig to 1,000 psig 10000 0 psig to 10,000 psig 100000 0 psig to 100,000 psig 200A 0 psia to 200 psia |
|  | 30/300 |  | 0 psig to 1,500 psig 15000 0 psig to 15,000 psig 115000 0 psig to 115,000 psig 300A 0 psia to 300 psia |
|  |  |  | Other ranges available on request Note: 616 Series is available for pressure ranges up to 0 psig to 8,000 psig |
| ACCURACIES | 1 | ±0.25% full scale (BFSL) 2 | ±0.125% full scale (BFSL) |
| OUTPUT SIGNALS | 1 | 4 mA to 20 mA, 2-wire 3 | 1 Vdc to 5 Vdc, 3-wire NOTE: 0 Vdc to 5 Vdc and 0 Vdc to 10 Vdc outputs are also available in 4-wire configurations for use with other electrical systems. 0 Vdc to 10 Vdc, 3-wire |
|  | 2 | 0 Vdc to 5 Vdc, 3-wire 5 |  |
| PROCESS 615: | 2 | 1/4″ NPT male 6 | 9/16″ -18 UNF 2B high pressure cone ** 8 1/2″ NPT male |
| CONNECTIONS |  |  | (Standard on 30,000 to 120,000 psig) |
| 616: | 11 | G 1/2 B (Pressure ranges ≥ 0 psig to 30 psig) 13 | G 1 B (Pressure ranges ≤ 0 psig to 30 psig) Other connections available upon request |
| ELECTRICAL CONNECTIONS | 1 3 | 36″ cable (connected to option 8) 8 6-pin Bendix 14 | Hirschmann (DIN EN 175301-803 Form A) 25 M12 x 1 (4-pin) Hirschmann type with 1/2″ NPT female conduit 36 Integral 36″ cable |
|  | 6 | 1/2″ NPT conduit w/ 36″ cable |  |
| OPTIONS | ST8 | SS Threaded Orifice G1 | G 1 Weld-on adapter (616 only) G½ G 1/2 Weld-on adapter (616 only) |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

* Not available with 1/4" NPT

** Equivalent to F250C Parker Autoclave

EXAMPLE	615 – 500 – 1 – 1 – 8 – 1 – ST8

Series	615 Series

Pressure range	0 psig to 500 psig

Accuracy	±0.25% full scale (BFSL)

Output signal	4 mA to 20 mA, 2-wire

Process connection	1/2" NPT Male

Electrical connection	36" cable

Option	Threaded Orifice

1.36″ (34.5 mm)

1.89"

(48 mm)	1.06" sq.

(27 mm)

1.10"

(28 mm)

1/2″ NPT Conduit with 36″ jacketed cable

0.68"

1.48"

(37.5 mm)

(17.3 mm)

Integral 36″ cable

*6 pin Bendix

0.51"

(13 mm)

0.54"

(13.8 mm)

*M12 x 1 (4-pin)

1.65"

(42 mm)

Hirschmann with

1/2″ NPT Female

1.06" sq.

(27 mm)

  - " HEX

(27 mm) 1/2" NPT

1.06"

(27 mm)

2.16"

(55 mm)

0.75"

(19 mm)

2-WIRE WIRING

*Note: mate supplied

separately or customer supplied

    - WIRE WIRING

ISO 4400 conduit

Hirschmann

615/616 SERIES	INFORMATION

ORDERING

DIMENSIONS

NOTE

See 621/622 Series for G1/2B and G1B Front Flush Process

Connection Dimensions pg. 85

|  | Hirschmann | Cable | M12 | Bendix |
| --- | --- | --- | --- | --- |
| + Supply | 1 | Red | 1 | A |
| Common | 2 | Black | 3 | B |
| + Output | 3 | White | 4 | C |

|  | Hirschmann | Cable | M12 | Bendix |
| --- | --- | --- | --- | --- |
| + Supply | 1 | Red | 1 | A |
| + Output | 2 | Black | 3 | B |

73

APPLICATIONS

    - Aerospace equipment

    - Laboratory & test equipment

    - Precision measurement

SERIES

640

Vacuum ranges through 0 psig to 15,000 psig; absolute ranges from 0 psia to 15 psia through 0 psia to 300 psia

- Standard 4 mA to 20 mA output

- 316 and 17-4PH Stainless Steel wetted parts

- CE compliant to suppress RFI, EMI and ESD

SPECIFICATIONS

Output signals	4 mA to 20 mA, 2-wire; 0 Vdc to 5 Vdc and 0 Vdc to 10 Vdc, 3-wire

Pressure ranges	Vacuum through 0 psig to 15,000 psig

Absolute from 0 to 15 psia through 0 psia to 300 psia

Accuracy	±0.05% full scale (BFSL); optional ±0.025% full scale (BFSL); (includes the ef- fects of non-linearity, hysteresis, non-repeatability, zero point and full scale errors)

Stability	≤ ±0.1% full scale; 5 psi ±0.2% full scale per year Response time	< 300 ms (between 10% to 90% full scale) Service life	> 100,000,000 load cycles

Temperature ranges	Compensated 32 °F to 160 °F (0 °C to 70 °C)

Effect: ±0.005% °F (32 °F to 50 °F) to zero point and pressure range no effect (50 °F to 104 °F) for zero and span

±0.005%/ °F (104 °F to 158 °F) to zero point and pressure range Media - 5 °F to 160 °F (-20 °C to 70 °C)

Ambient 32 °F to 160 °F (0 °C to 70 °C)

Storage -5 °F to 160 °F (-20 °C to 70 °C)

Power requirement*	9 Vdc to 30 Vdc (4 mA to 20 mA, 2-wire, 0 Vdc to 5 Vdc, 3-wire)

14 Vdc to 30 Vdc (0 Vdc to 10 Vdc, 3-wire) Voltage supply via RS232 interface (RS232)

Load limitations	≤ (VPower-10)/0.020 Amp for 4 mA to 20 mA

≥ 10,000 Ω for 0 Vdc to 10 Vdc, 3-wire

≥ 5,000 Ω for 0 Vdc to 5 Vdc, 3-wire

Proof pressure	3 times full scale for ranges 0 psi to 5 psi through 0 psi to 200 psi

2 times full scale for ranges 0 psi to 300 psi through 0 psi to 10,000 psi

1.5 times full scale for 0 psi to 15,000 psi

Burst pressure	4 times full scale for ranges 0 psi to 5 psi through 0 psi to 200 psi

4 times full scale for ranges 0 psi to 300 psi through 0 psi to 10,000 psi 3 times full scale for 0 psi to 15,000 psi

Measuring element	316 Stainless Steel for vacuum through 300 psi;

17-4PH Stainless Steel for ≥500 psi

Connection	316 Stainless Steel

Housing material	316 Stainless Steel

Environmental rating	IP65

Electromagnetic rating	CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity, overvoltage and short circuit protection

Shock	100 g’s according to IEC 60068-2-27

Vibration	15 g’s according to IEC 60068-2-6

Weight	Approximately 11 oz.

- Unregulated

Industrial Pressure T ransmitters & T ransducers

Precision Heavy-Duty

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

74	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| SERIES 640 |  |  |  |  |  |  |
| PRESSURE RANGES | 30vac 30/15 | -30 inHg to 0 psig 30/300 -30 inHg to 300 psig 150 -30 inHg to 15 psig 5 0 psig to 5 psig 200 -30 inHg to 30 psig 10 0 psig to 10 psig 300 -30 inHg to 60 psig 15 0 psig to 15 psig 500 -30 inHg to 100 psig 30 0 psig to 30 psig 750 -30 inHg to 150 psig 60 0 psig to 60 psig 1000 -30 inHg to 200 psig 100 0 psig to 100 psig 2000 psig = gauge pressure psia = absolute pressure |  | 0 psig to 150 psig 3000 0 psig to 3,000 psig 0 psig to 200 psig 5000 0 psig to 5,000 psig 0 psig to 300 psig 6000 0 psig to 6,000 psig 0 psig to 500 psig 7500 0 psia to 7,500 psig 0 psig to 750 psig 10000 0 psia to 10,000 psig 0 psig to 1,000 psig 15000 0 psia to 15,000 psig 0 psig to 2,000 psig 15A 0 psia to 15 psia Other ranges available on request | 30A 60A | 0 psia to 30 psia 0 psia to 60 psia |
|  | 30/30 |  |  |  | 100A | 0 psia to 100 psia |
|  | 30/60 |  |  |  | 150A | 0 psia to 150 psia |
|  | 30/100 |  |  |  | 200A | 0 psia to 200 psia |
|  | 30/150 |  |  |  | 300A | 0 psia to 300 psia |
|  | 30/200 |  |  |  |  |  |
| ACCURACIES | 1 | ±0.05% full scale (BFSL) | 2 | ±0.025% full scale (BFSL) |  |  |
| OUTPUT SIGNALS | 1 | 4 mA to 20 mA, 2-wire analog | 5 | 0 Vdc to 10 Vdc, 3-wire analog |  |  |
|  | 2 | 0 Vdc to 5 Vdc, 3-wire analog |  |  |  |  |
| PROCESS CONNECTIONS | 2 | 1/4″ NPT male | 8 | 1/2″ NPT male; other connections available upon request |  |  |
| ELECTRICAL CONNECTIONS | 1 | 54″ Integral cable | 25 | M12 x 1 (4-pin) |  |  |
| OPTION | ST8 | Threaded Orifice |  |  |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

EXAMPLE	640 – 3000 – 1 – 1 – 8 – 25 – ST8

Series	640 Series

Pressure range	0 psig to 3,000 psig

Accuracy	±0.05% full scale (BFSL)

Output signal	4 mA to 20 mA, 2-wire analog

Process connection	1/2" NPT Male

Electrical connection	M12 x 1 (4-pin)

Option	Threaded Orifice

0.71" (18 mm)

2.95"

(75 mm)

1.06" HEX

(27 mm)

0.51" (13 mm)

1/4" NPT

2-WIRE WIRING

1.06"

(27 mm)

| Wiring | M12 | Cable |
| --- | --- | --- |
| + Supply | 1 | Brown |
| Common | 3 | Blue |
| + Output | 4 | Black |

WIRE WIRING

640 SERIES	INFORMATION

ORDERING

DIMENSIONS

| Wiring | M12 | Cable |
| --- | --- | --- |
| + Supply | 1 | Brown |
| + Output | 3 | Blue |

75

APPLICATIONS

  - Hydraulics & pneumatics

  - Mobile hydraulics

  - Power generation

  - Pumps & compressors

  - Refrigeration controls

SERIES

660

Ranges from 0 psig to 200 through 0 psig to 15,000 psig

- Current & voltage outputs available

- Stainless Steel wetted parts

- 1.0 mm standard orifice size for improved performance in dynamic

applications

- CE compliant to suppress RFI, EMI and ESD

SPECIFICATIONS

Output signals	4 mA to 20 mA 2-wire, 1 Vdc to 5 Vdc 3-wire; 0.1 Vdc to 10 Vdc, 3-wire

Pressure ranges	0 psig to 200 psig through 0 psig to 15,000 psig

Accuracy	±0.25% full scale (BFSL); (Includes the effects of non-linearity, hysteresis,

non-repeatability, zero point and full scale errors)

Stability	≤ ±2% full scale for 1 year, non-accumulating Response time	<2 ms (between 10% and 90% full scale) Service life	> 100,000,000 load cycles

Temperature ranges	Compensated -4 °F to 185 °F (-20 °C to 85 °C)

Zero effect ±0.01% full scale/ °F Span effect ±0.01% full scale/ °F

Media -13 °F to 185 °F (-40 °C to 100 °C); -40 °F to 257 °F (-40 °C to 125 °C)

available on request

Ambient -4 °F to 185 °F (-25 °C to 85 °C)

Storage -40 °F to 212 °F (-40 °C to 100 °C)

Power requirement*	10 Vdc to 36 Vdc (4 mA to 20 mA, 2-wire)

8 Vdc to 36 Vdc (1 Vdc to 5 Vdc, 3-wire)

14 Vdc to 36 Vdc (0.1 Vdc to 10 Vdc, 3-wire)

Load limitations	≤ (VPower-10)/0.020 Amp for 4 mA to 20 mA

≥ 10,000 Ω for 1 Vdc to 10 Vdc, 3-wire

≥ 5,000 Ω for 1 Vdc to 5 Vdc, 3-wire

Proof pressure	2 times full scale for ranges 0 psi to 200 psi through 0 psi to 10,000 psi

1.5 times full scale for 0 psi to 15,000 psi range

Burst pressure	9 times full scale for 0 psi to 200 psi through 0 psi to 1,000 psi

3 times full scale for ranges 0 to 3,000 psi through 0 psi to 15,000 psi

Measuring element	17-4PH Stainless Steel

Connection	316 Stainless Steel

Housing material	316 Stainless Steel

Environmental rating	IP65; IP67 M12x1 electrical connection for pressure ranges 0 psig to 1,500 psig

or higher

Electromagnetic rating CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity, over-voltage and short circuit protection

Shock	1,000 g’s according to IEC 60068-2-27

Vibration	20 g’s according to IEC 60068-2-6

Weight	Approximately 1.75 oz.

Industrial Pressure T ransmitters & T ransducers

Micro-Size

* Unregulated

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

76	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| SERIES 660 |  |  |  |  |
| PRESSURE RANGES | 200 300 | 0 psig to 200 psig 500 0 psig to 500 psig 3000 0 psig to 3,000 psig 0 psig to 300 psig 1000 0 psig to 1,000 psig 5000 0 psig to 5,000 psig psig = gauge pressure Other ranges available on request | 10000 15000 | 0 psig to 10,000 psig 0 psig to 15,000 psig |
| ACCURACY | 1 | ±0.25% full scale (BFSL) |  |  |
| OUTPUT SIGNALS | 1 | 4 mA to 20 mA, 2-wire 3 1 Vdc to 5 Vdc, 3-wire 27 0.1 Vdc to 10 Vdc, 3-wire |  |  |
| PROCESS CONNECTIONS | 2 | 1/4″ NPT male |  |  |
| ELECTRICAL CONNECTIONS | 1 | 36″ cable (connected to option 7) 7 Mini-Hirschmann (DIN EN 175301-803 Form C) | 25 | M12 x 1 (4-pin) |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

EXAMPLE	660 – 500 – 1 – 1 – 2 – 25

Series	660 Series

Pressure range	0 psig to 500 psig

Accuracy	±0.25% full scale (BFSL)

Output signal	4 mA to 20 mA, 2-wire

Process connection	1/4" NPT Male

Electrical connection	M12 x 1 (4-pin)

1.40"

(35.5 mm)

0.63" sq

(15.8 mm)

0.44"

(11 mm)

1.06"

(26.8 mm)

1.73"

(44 mm)

0.78”

(19.8 mm)

1.83"

(46.5 mm)

0.75" HEX

(19 mm)

1/4" NPT

0.75"

(19 mm)	0.51"

(13 mm)

M12 x 1 (4-pin)

2-WIRE WIRING

Mini-Hirschmann

3-WIRE WIRING

660 SERIES	INFORMATION

ORDERING

DIMENSIONS

| Wiring | M12 | Mini-Hirschmann | Cable |
| --- | --- | --- | --- |
| + Supply | 1 | 1 | Red |
| Common | 3 | 2 | Black |
| + Output | 4 | 3 | White |

| Wiring | M12 | Mini-Hirschmann | Cable |
| --- | --- | --- | --- |
| + Supply | 1 | 1 | Red |
| + Output | 3 | 2 | Black |

77

APPLICATIONS

  - Hydraulics & pneumatics

  - Power generation

  - Pumps & compressors

  - Stamping & forming presses

  - Water & wastewater

SERIES

800

Compound and standard ranges from 0 psig to 10 psig through 0 psig to 7,500 psig

- 316L Stainless steel wetted parts

- Current and voltage outputs available

- 7 different output configurations available

- Display and electrical connection can be rotated independently

- CE compliant to suppress RFI, EMI and ESD

- RoHS compliant

SPECIFICATIONS

Pressure ranges

Compound and standard ranges from 0 psig to 10 psig through

0 psig to 7,500 psig

Switching parameters	Individually adjustable via external control keys

Number	1 or 2 (PNP or NPN)

Function	N.O., N.C., window, hysteresis (freely adjustable)

Contact rating	250 mA max.

Response time	≤5 ms

Accuracy	≤ 0.5 % of span

Switch point	.25 to 100% of full scale

Hysteresis	Fully adjustable

Transmitter parameters

Output signal	4 mA to 20 mA or 0 Vdc to 10 Vdc; programmable and freely adjustable Accuracy	≤±0.5% of span including non-linearity, hysteresis, zero offset and end value

deviation (corresponds to measured error per IEC 61298-2)

Non-repeatability	< 0.1% of span (IEC 61298-2)

Adjustment	Freely scalable within the range of 5:1

Service life	100,000,000 load cycles

Temperature ranges	Compensated 32 °F to 176 °F (0 °C to 80 °C)

Media -4 °F to 185 °F (-20 °C to 185 °C)

Ambient -4 °F to 176 °F (-20 °C to 80 °C)

Storage -4 °F to 158 °F (-20 °C to 70 °C)

Display	14 segment-LED, red 4-digit, height 0.35”

Power requirement*	15 - 35 Vdc

Max. 45 mA for versions without 4-20 mA output signal,

Industrial Pressure T ransmitters & T ransducers

Electronic Indicating Transmitter/Switch

Current consumption	Max. 70 mA for versions with 4-20 mA output signal,

Total consumtpion max. 600 mA including switching current

Proof pressure	2 times full scale

Measuring element	<150 psi: 316L Stainless steel

≥150 psi: 316L, PH grade Stainless steel

Housing material	304 Stainless steel

Connection	316 stainless steel

Environmental rating	IP65 and IP67 per IEC 60529

Electromagnetic rating	CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Protected against reverse polarity, over-voltage and short circuit

Shock	> 50 g’s according to IEC 60068-2-27

Vibration	> 20 g’s according to IEC 60068-2-6

Weight	Approx 0.49 lb.

* Unregulated

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

78	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| SERIES | 800 | 304 Stainless steel housing |  |  |
| SWITCH FUNCTIONS | 1 2 3 4 | 2 N.O. or N.C. (PNP or NPN) 1 N.O. or N.C. (PNP or NPN) with 4 mA to 20 mA 3-wire analog output - N.O. or N.C. (PNP or NPN) with 0 Vdc to 10 Vdc 3-wire output - N.O. or N.C. (PNP or NPN) with 4 mA to 20 mA analog output* | 5 6 7 | 2 N.O. or N.C. switch (PNP/NPN) with 0 Vdc to 10 Vdc 3-wire output * - N.O. or N.C. switch (PNP/NPN) with 4 mA to 20 mA/0 Vdc to 10 Vdc 3-wire output 2 ** - N.O. or N.C. switch (PNP/NPN) with 4 mA to 20 mA/0 Vdc to 10 Vdc 3-wire output *, ** |
| PROCESS CONNECTIONS | 2 8 | 1/4″ NPT male 10 G 1/4 B male 1/2″ NPT male 11 G 1/2 B male | 45 | SAE J514 FIG B (Non-Adjustable) |
| ADJUSTABLE RANGES (Max. working pressure) | 14.5vac 14.5/15 14.5/30 14.5/50 14.5/100 14.5/160 14.5/200 14.5/300 10 | -14.5 psig to 0 psig 15 0 psig to 15 psig -14.5 psig to 15 psig 25 0 psig to 25 psig -14.5 psig to 30 psig 30 0 psig to 30 psig -14.5 psig to 50 psig 50 0 psig to 50 psig -14.5 psig to 100 psig 100 0 psig to 100 psig -14.5 psig to 160 psig 160 0 psig to 160 psig -14.5 psig to 200 psig 200 0 psig to 200 psig -14.5 psig to 300 psig 300 0 psig to 300 psig 0 psig to 10 psig 500 0 psig to 500 psig | 1000 1500 2000 3000 5000 7500 10A 15A 25A | 0 psig to 1,000 psig 30A 0 psia to 30 psia 0 psig to 1,500 psig 50A 0 psia to 50 psia 0 psig to 2,000 psig 100A 0 psia to 100 psia 0 psig to 3,000 psig 160A 0 psia to 160 psia 0 psig to 5,000 psig 200A 0 psia to 200 psia 0 psig to 7,500 psig 300A 0 psia to 300 psia 0 psia to 10 psia 0 psia to 15 psia 0 psia to 25 psia |
| ELECTRICAL CONNECTIONS 2 M12 x 1 (4-pin) 3 M12 x 1 (5-pin), 2 switch and analog output |  |  |  |  |
| OPTIONS | ST8 | Threaded Orifice |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

* Available only with a M12 x 1 (5-pin) connector

** Can switch between 4 mA to 20 mA / 0 Vdc to 10 Vdc

EXAMPLE	800 – 1 – 2 – 160 – 2 – ST8

Series	800 Series

Switch function	2 N.O. or N.C. (PNP or NPN)

Process connection	1/4" NPT Male

Adjustable range	0 psig to 160 psig

Electrical connection	M12 x 1 (4-pin)

Option	Threaded Orifice

1 switching output (M12x1) with 4 mA to 20 mA signal† p-switching

1 switching output (M12x1) with 4 mA to 20 mA signal† n-switching

≈Ø1.50"

x 1

1.06" HEX

(27 mm)

1.16"

(29.5 mm)

1/4" NPT

Display rotates >300°

(38 mm)

2 switching output (M12x1)

1.42"

4	3

power supply

sig. output

1	2

S1 output

4	3

power supply

sig. output

1	2

S1 output

(36 mm)

2 switching output (M12x1)

M12

power supply

4	3

S2 output

1	2

S1 output

power supply

4	3

S2 output

1	2

S1 output

p-switching

2 switching output (M12x1) with 4 mA to 20 mA signal†

4	3

power supply

5

S2 output

1	2

S1 output

sig. output

p-switching

n-switching

- switching output (M12x1) with 4 mA to 20 mA signal† n-switching

2.83"

(72 mm)

1.02"

(26 mm)

.51"

power supply

4

S2 output

1

S1 output

sig. output

2

5

3

(13 mm)

Ø1.38"

(35 mm)

Electrical Connection rotates >300°

800 SERIES	INFORMATION

ORDERING

DIMENSIONS

† Also applies to 0 Vdc to 10 Vdc output	79

#### OEM Pressure T ransmitters & T ransducers

Compact

300

SERIES

##### Ranges from 0 psig to 15 through 0 psig to 10,000 psig; absolute ranges from 0 psia to 15 psia through 0 psia to 300 psia

- Current and voltage outputs available

- 316 and 13-8PH Stainless Steel wetted parts

- RoHS compliant

- CE compliant to suppress RFI, EMI and ESD

###### APPLICATIONS

- HVAC

- Hydraulics & pneumatics

- Injection molding machines

- Railroad equipment

- Stamping & forming presses

SPECIFICATIONS

Output signals	4 mA to 20 mA, 2-wire; 0 Vdc to 5 Vdc, 3-wire; 1 Vdc to 5 Vdc, 3-wire; 0 Vdc to 10 Vdc, 3-wire; 0.5 Vdc to 4.5 Vdc ratiometric, 3-wire

Pressure ranges	0 psig to 15 psig through 0 psig to 10,000 psig

Absolute from 0 psia to 15 psia through 0 psia to 300 psia

Accuracy	±0.5% full scale (BFSL); optional ±0.25% full scale (BFSL); (includes the effects of non-linearity, hysteresis, non-repeatability, zero point and full scale errors)

Stability	≤ ±0.2% full scale per year, non-accumulating Response time	≤ 4 ms (between 10% and 90% full scale) Service life	> 100,000,000 load cycles

Temperature ranges	Compensated 32 °F to 176 °F (0 °C to 80 °C)

Media 32 °F to 176 °F (0 °C to 80 °C)

Ambient 32 °F to 176 °F (0 °C to 80 °C)

Storage -4 °F to 176 °F (0 °C to 80 °C)

Power requirement*	8 Vdc to 30 Vdc (4 mA to 20 mA, 2-wire, 0 Vdc to 5 Vdc, 3-wire, 1 Vdc to 5 Vdc, 3-wire, 0.5 Vdc to 4.5 Vdc, 3-wire)

14 Vdc to 30 Vdc (0 Vdc to 10 Vdc, 3-wire)

5 Vdc ± 10% (0.5 Vdc to 4.5 Vdc ratiometric, 3-wire)

Load limitations	≤ (VPower−10)/0.020 Amp for 4 mA to 20 mA output

≤ 5,000 Ω for 1 Vdc to 5 Vdc output

≤ 10,000 Ω for 0 Vdc to 10 Vdc output

≤ 4,500 Ω for 0.5 Vdc to 4.5 Vdc output

Proof pressure	2 times full scale

Burst pressure	6 times full scale

Measuring element	316 Stainless Steel for absolute through 150 psi

13-8PH Stainless Steel for ≥150 psi

Connection	316 Stainless Steel

Housing material	316 Stainless Steel

Environmental rating	IP65 to IP67 depending on electrical connection

Electromagnetic rating CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity, over-voltage and short circuit protection

Shock	500 g’s according to IEC 60068-2-27

Vibration	10 g’s according to IEC 60068-2-6

Weight	Approximately 2.8 oz.

* Unregulated

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

80	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SERIES 300 |  |  |  |  |  |
| PRESSURE RANGES | 15 0 psig to 15 psig 300 0 psig to 300 psig 3000 30 0 psig to 30 psig 500 0 psig to 500 psig 5000 |  | 0 psig to 3,000 psig 0 psig to 5,000 psig | 30A 60A | 0 psia to 30 psia 0 psia to 60 psia |
|  | 60 0 psig to 60 psig 750 0 psig to 750 psig 6000 |  | 0 psig to 6,000 psig | 100A | 0 psia to 100 psia |
|  | 100 0 psig to 100 psig 1000 0 psig to 1,000 psig 7500 |  | 0 psig to 7,500 psig | 150A | 0 psia to 150 psia |
|  | 150 0 psig to 150 psig 1500 0 psig to 1,500 psig 10000 |  | 0 psig to 10,000 psig | 200A | 0 psia to 200 psia |
|  | 200 0 psig to 200 psig 2000 0 psig to 2,000 psig 15A |  | 0 psia to 15 psia | 300A | 0 psia to 300 psia |
|  | psig = gauge pressure psia = absolute pressure Other ranges available upon request. |  |  |  |  |
| ACCURACIES | 1 ±0.5% full scale (BFSL) 2 ±0.25% full scale (BFSL) |  |  |  |  |
| OUTPUT SIGNALS | - 4 mA to 20 mA, 2-wire 3 - 0 Vdc to 5 Vdc, 3-wire 5 | 1 Vdc to 5 Vdc, 3-wire 13 0 Vdc to 10 Vdc, 3-wire | 0.5 Vdc to 4.5 Vdc, 3-wire (ratiometric) |  |  |
| PROCESS CONNECTIONS | 2 1/4″ NPT male 10 G 1/4 B 45 8 1/2″ NPT male 11 G 1/2 B |  | SAE J514 FIG B (Non-Adjustable) |  |  |
| ELECTRICAL CONNECTIONS | 1 36″ cable (connected to option 8) 8 |  | Hirschmann (DIN EN 175301- | 25 | M12 x 1 (4-pin) |
|  |  |  | 803 form A) |  |  |
|  | 7 Mini-Hirschmann (DIN EN 175301-803 form C) 14 |  | Hirschmann type with 1/2″ | 36 | 6' Integral cable |
|  |  |  | NPT female conduit |  |  |
| OPTION | ST8 Threaded Orifice (0.3 mm) |  |  |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

EXAMPLE	300  –  500  –  1  –  1  –  2 –  8 –  ST8

Series	300 Series

Pressure range	0 psig to 500 psig

Accuracy	±0.50% full scale (BFSL)

Output signal	4 mA to 20 mA, 2-wire

Process connection	1/4" NPT Male

Electrical connection	Hirschmann

Option	Threaded Orifice

0.51″

(13 mm)

1.14″

1.85″

(47 mm)

  - ″ sq

0.36″

(9 mm)

0.80″

1.40″

(35.5 mm)	0.63″ sq

(15.8 mm)

(29 mm)

(27 mm)

(20.3 mm)

0.47″ sq

1.10″

(27.8 mm)

0.78″

(19.7 mm)

1.06″

(26.8 mm)

(12 mm)

1.12″ sq

(28.5 mm)

1.29″

(32.8 mm)

Integral cable	Mini-Hirschmann

*M12 x 1 (4-pin)

* Note: (mate supplied separately)

1.06″ HEX

(27 mm)

1/4″ NPT

Hirschmann

0.51″

(13 mm)

300 SERIES	INFORMATION

ORDERING

DIMENSIONS

3-WIRE WIRING

| Wiring | M12 | Hirschmann | Cable |
| --- | --- | --- | --- |
| + Supply | 1 | 1 | Brown |
| Common | 3 | 2 | Blue |
| + Output | 4 | 3 | White |

2-WIRE WIRING

| Wiring | M12 | Hirschmann | Cable |
| --- | --- | --- | --- |
| + Supply | 1 | 1 | Brown |
| + Output | 3 | 2 | Blue |

81

APPLICATIONS

    - Hydraulics & pneumatics

    - Mobile hydraulics

    - Pumps & compressors

    - Refrigeration controls

    - Transportation

SERIES

650

Ranges from 0 psig to 100 psig through 0 psig to 8,000 psig

- Current and voltage outputs available

- Stainless Steel wetted parts

- CE compliant to suppress RFI, EMI and ESD

SPECIFICATIONS

Output signals	4 mA to 20 mA 2-wire, or 1 Vdc to 5 Vdc 3-wire

Pressure ranges	0 psig to 100 psig through 0 psig to 8,000 psig

Accuracy	±0.50% full scale (BFSL) (Includes the effects of non-linearity, hysteresis,

non-repeatability, zero point and full scale errors)

Stability	±0.2% full scale for 1 year, non-accumulating

Response time	< 5 ms (between 10% and 90% full scale); restrictor port I.D. to

dampen pulsations

Service life	> 100,000,000 load cycles

Temperature ranges	Compensated 32 °F to 176 °F (0 °C to 80 °C)

Zero effect ±0.008% full scale/ °F Span effect ±0.008% full scale/ °F

Media -40 °F to 257 °F (-40 °C to 125 °C)

Ambient -40 °F to 212 °F (-40 °C to 100 °C)

Storage -40 °F to 248 °F (-40 °C to 120 °C)

Power requirement*	8 Vdc to 36 Vdc (4 mA to 20 mA, 2-wire, 0 Vdc to 5 Vdc, 3-wire, 1 Vdc to 5 Vdc, 3-wire, 0.5 Vdc to 4.5 Vdc, 3-wire)

14 Vdc to 36 Vdc (0 Vdc to 10 Vdc, 3-wire)

5 Vdc ± 10% (0.5 Vdc to 4.5 Vdc ratiometric, 3-wire)

Load limitations	≤ (VPower−10)/0.020 amp for 4 mA to 20 mA output

≤ 5,000 Ω for 1 Vdc to 5 Vdc output

≤ 10,000 Ω for 0 Vdc to 10 Vdc output

≤ 4,500 Ω for 0.5 Vdc to 4.5 Vdc output

Proof pressure	2 times full scale

Burst pressure	8 times full scale for ranges 0 psi to 100 psi through 0 psi to 1,500 psi

4 times full scale for ranges 0 psi to 2,000 psi through 0 psi to 8,000 psi

Measuring element	17-4PH Stainless Steel Connection	316 Stainless Steel Housing material	PBT - fiber reinforced plastic

Environmental rating	IP67 for M12x1 (4-pin) electrical connection and Metri-Pack connection; IP69K (steam jet cleaning) for cable connection

Electromagnetic rating CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity, over-voltage and short circuit protection

Shock	500 g’s according to IEC 60068-2-27

Vibration	20 g’s according to IEC 60068-2-6

Weight	Approximately 2.5 oz.

OEM Pressure T ransmitters & T ransducers

High Volume

* Unregulated

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

82	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SERIES 650 |  |  |  |  |  |  |  |  |  |  |
| PRESSURE RANGES | 100 150 | 0 psig to 100 psig 0 psig to 150 psig | 300 0 psig to 300 psig 400 0 psig to 400 psig 500 0 psig to 500 psig Other ranges available on request |  | 600 750 | 0 psig to 600 psig 0 psig to 750 psig | 1500 2000 | 0 psig to 1,500 psig 0 psig to 2,000 psig | 5000 8000 | 0 psig to 5,000 psig 0 psig to 8,000 psig |
|  | 200 | 0 psig to 200 psig |  |  | 1000 | 0 psig to 1,000 psig | 3000 | 0 psig to 3,000 psig |  |  |
|  |  | psig = gauge pressure |  |  |  |  |  |  |  |  |
| ACCURACY | 1 | ±0.5% full scale (BFSL) |  |  |  |  |  |  |  |  |
| OUTPUT SIGNALS | 1 | 4 mA to 20 mA, 2-wire | 3 | 1 Vdc to 5 Vdc, 3-wire | 5 | 0 Vdc to 10 Vdc, 3-wire | 13 | 0.5 Vdc to 4.5 Vdc ratiometric, 3-wire |  |  |
| PROCESS | 2 | 1/4″ NPT male | 24 | 7/16 - 20 2B Schrader | 45 | SAE J514 FIG B (Non-Adjustable) |  |  |  |  |
| CONNECTIONS | 10 | G1/4B male | 35 | 7/16 - 20 SAE with 45° flare |  |  |  |  |  |  |
| ELECTRICAL CONNECTIONS | 25 34 | M12 x 1 (4-pin) Metri-Pack 150 series | 36 39 | 18″ Integral cable IP67 18″ Integral cable IP69K | 45 46 | AMP Superseal 1.5 Deutsch (3-pin) DT04-3P |  |  |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for minimum quantity requirements and delivery information.

EXAMPLE	650 – 500 – 1 – 1 – 2 – 25

Series	650 Series

Pressure range	0 psig to 500 psig

Accuracy	±0.5% full scale

Output signal	4 mA to 20 mA, 2-wire

Process connection	1/4" NPT Male

Electrical connection	M12 x 1 (4-pin)

0.78″ (19.7 mm)

0.36″

(9 mm)

0.80″ (20.3 mm)

0.78″ (19.7 mm)

1.47″ (37.3 mm)

0.67″

1.41″ (35.8 mm)

0.81″ (20.5 mm)

1.48″ (37.7 mm)

(17 mm)

0.63″

1.43"

(36.2 mm

(17 mm)

)

0.80″ (20.2 mm)

0.47″

(12 mm)

1.47″ (37.3 mm)

18″ Integral cable	Metri-Pack

AMP Superseal 1.5

Deutsch (3-pin)

150 Series

  - WIRE WIRING

DT04-3P

  - WIRE WIRING

  - ″ HEX

(22 mm) 1/4″ NPT

M12 X 1

(4-pin)

0.51″

(13 mm)

650 SERIES	INFORMATION

ORDERING

DIMENSIONS

| Wiring | Cable | M12 | Metri- Pack | AMP Superseal | Deutsch DT04-3P |
| --- | --- | --- | --- | --- | --- |
| + Supply | Brown | 1 | B | 3 | A |
| + Output | Black | 3 | A | 1 | B |

| Wiring | Cable | M12 | Metri- Pack | AMP Superseal | Deutsch DT04-3P |
| --- | --- | --- | --- | --- | --- |
| + Supply | Brown | 1 | B | 3 | A |
| Common | Green | 3 | A | 1 | B |
| + Output | White | 4 | C | 2 | C |

83

non-repeatability, zero point and full scale errors)

Stability	≤±0.2% full scale for 1 year, non-accumulating Response time	≤1 ms (between 10% and 90% full scale) Service life	>100,000,000 load cycles

###### APPLICATIONS

Temperature ranges	Compensated

Zero effect Span effect

32 °F to 176 °F (0 °C to 80 °C)

±0.011% full scale/ °F

±0.011% full scale/ °F

Hazardous Location Pressure T ransmitters

Explosion-Proof

APPROVED

621/622 SERIES

- Vacuum and compound ranges through 0 psig to 15,000 psig; absolute ranges from 0 psia to 15 psia through 0 psia to 100 psia

- Current and voltage outputs available

- 316 Stainless Steel and Elgiloy wetted parts

- CE compliant to suppress RFI, EMI and ESD

- NACE MR0175/ISO 15156 compliant

- NSI/ISA-12.27.01-2003 approved single seal

SPECIFICATIONS

Output signals	4 mA to 20 mA, 2-wire; 1 Vdc to 5 Vdc, 3-wire; 0.5 Vdc to 4.5 Vdc, 3-wire

Pressure ranges	Vacuum through 0 psi to 15,000 psi

Absolute from 0 psia to 15 psia through 0 psia to 100 psia

Accuracy	±0.25% full scale (BFSL) (Includes the effects of non-linearity, hysteresis,

Chemical processing

    - Gas pressure measurement

    - Oil field & offshore

    - Mining

    - Well head measurement

NOSHOK 621 and 622 Sereis transmitters are Factory Mutual and Canadian Standards Association approved for use in hazardous location applications as follows:

Explosion-proof with entity approve for: Class I, Division 1, Groups A, B, C and D. Dust Ignition-proof with entity approval for class II/ III, Division 1, Groups E, F and G. Maximum electrical ratings 30V, 20 mA.

CE compliant with pressure equipment directive 97/23EC. ANSI/ISA-12.27.01-2003, Approved single seal.

84

Media	T6: -40 °F to 131 °F (-40 °C to 55 °C)

T5: -40 °F to 158 °F (-40 °C to 70 °C)

T4: -40 °F to 212 °F (-40 °C to 100 °C)

Ambient	T6: -40 °F to 140 °F (-40 °C to 60 °C)

T5: -40 °F to 167 °F (-40 °C to 75 °C)

T4: -40 °F to 221 °F (-40 °C to 105 °C)

Storage	-40 °F to 221 °F (-40 °C to 105 °C)

Power requirement*	10 Vdc to 30 Vdc (4 mA to 20 mA, 2-wire)

6 Vdc to 30 Vdc (1 Vdc to 5 Vdc, 3-wire, 0.5 Vdc to 4.5 Vdc, 3-wire)

14 Vdc to 30 Vdc (0 Vdc to 10 Vdc, 3-wire)

Load limitations	≤ (VPower-10)/0.020 Amp for 4 mA to 20 mA

≥ 10,000 Ω for 1 Vdc to 5 Vdc, 3-wire

Proof pressure	3 times full scale for ranges 0 psi to 15 psi through 0 psi to 200 psi

1.75 times full scale for ranges 0 psi to 300 psi through 0 psi to 10,000 psi

1.5 times full scale for 0 psi to 15,000 psi

Burst pressure	3.8 times full scale for ranges 0 psi to 15 psi through 0 psi to 200 psi

4 times full scale for ranges 0 psi to 300 psi through 0 psi to 10,000 psi 3 times full scale for 0 psi to 15,000 psi

Measuring element	621 Series is 316 Stainless Steel for ranges up through 0 psi to 300 psi, 316 Stainless Steel with Elgiloy ranges 0 psig to 500 psig and higher; 622 Series is 316 Stainless Steel with NBR o-ring; (FKM o-ring optional)

Connection	316 Stainless Steel

Housing material	316 Stainless Steel

Environmental rating	IP67

Electromagnetic rating CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity, over-voltage and short circuit protected

Shock	1,000 g’s according to IEC 60068-2-27

Vibration	20 g’s according to IEC 60068-2-6

Weight	Approximately 12 oz.

- Unregulated

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |
| --- | --- | --- | --- |
| SERIES | 621 Stainless Steel threaded connection | 622 316 Stainless Steel flush diaphragm | 622H Hastelloy C flush diaphragm |
| PRESSURE RANGES | 30vac -30 inHg to 0 psig 30/30 -30 inHg to 30 psig 30/60 -30 inHg to 60 psig 30/100 -30 inHg to 100 psig 30/160 -30 inHg to 160 psig 30/200 -30 inHg to 200 psig 30/300 -30 inHg to 300 psig psig = gauge pressure psia = absolute pressure | 5 0 psig to 5 psig 10 0 psig to 10 psig 15 0 psig to 15 psig 30 0 psig to 30 psig 60 0 psig to 60 psig 100 0 psig to 100 psig 200 0 psig to 200 psig Other ranges available on request | 300 0 psig to 300 psig 6000 0 psig to 6,000 psig 500 0 psig to 500 psig 8000 0 psig to 8,000 psig 1000 0 psig to 1,000 psig 10000 0 psig to 10,000 psig 1500 0 psig to 1,500 psig 15000 0 psig to 15,000 psig 2000 0 psig to 2,000 psig 15A 0 psia to 15 psia 3000 0 psig to 3,000 psig 100A 0 psia to 100 psia 5000 0 psig to 5,000 psig Note: 622 Series is available for pressure ranges up to 0 psig to 8,000 psig |
| ACCURACY | 1 ±0.25% full scale (BFSL) |  |  |
| OUTPUT SIGNALS | - 4 mA to 20 mA, 2-wire - 0 Vdc to 5 Vdc, 3-wire | 3 1 Vdc to 5 Vdc, 3-wire, low power 5 0 Vdc to 10 Vdc, 3-wire | 31 0.5 Vdc to 4.5 Vdc 3-wire, low power |
| PROCESS CONNECTIONS | 2 1/4″ NPT male 8 1/2" NPT male | 11 G 1/2 B * 13 G 1 B (622 Series only, <30 psig) |  |
| ELECTRICAL CONNECTIONS 6 1/2″ NPT male conduit with 6' integral cable 37 1/2″ NPT male conduit with 6' flying leads with epoxy seal |  |  |  |
| OPTIONS | ST8 Threaded Orifice (621 Series only) | 20 20′ Cable/lead (attached to electrical connection 6 or 37) | 30 30′ Cable/lead (attached to electrical connection 6 or 37) |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

* 622 Series only, G 1/2 B Flush (≥ 30 psig).

EXAMPLE	621 – 500 – 1 – 1 – 8 – 6 – ST8

Series	621 Series

Pressure range	0 psig to 500 psig

Accuracy	±0.25% full scale (BFSL)

Output signal	4 mA to 20 mA, 2-wire

Process connection	1/2" NPT Male

Electrical connection	1/2" NPT Male conduit with 6' integral cable

Option	Threaded Orifice

1.42″

0.61″

(15.5 mm)

Front flush process connections

(36 mm)

0.75″

(19 mm)

For ranges 0 psi to 30 psi through 0 psi to 8,000 psi

O-ring 0.73″ x 0.94" x 0.08″

(18.5mmx 23.9mm)

0.39″

(10mm)	O-ring 0.59″ x 0.08″ (15mmx 2mm)

ø.71″ ±.003

(18mm)

G1/2 B

1.06″ (27mm)

For ranges 0 to 30 psi and below

1.61″ (41mm)

0.81″ (20.5mm)

O-ring 1.17″ x 1.41″ x 0.08″ (29.7mmx 35.7mm)

1/2″ NPT

1.06″ HEX

(27 mm)

0.81″ (20.5mm)

0.39″

(10mm)

ø1.18″ ±.003

(30mm)

G1 B

O-ring 1.02″ x 0.08″ (26mmx 2mm)

2.56″

(65 mm)

Flush corresponding port weld-on adapters

1.06″ HEX

(27 mm)

1/2″ NPT

1.06″

0.41″ (10.5mm)

(27 mm)

0.75″

(19 mm)

621/622 SERIES	INFORMATION

ORDERING

DIMENSIONS

ø1.97″ (50mm)

ø.84″ ±.007

x

A

ø.72″ ±.007 (18.2mm)

G1/2

.76″ ±.003 (19.4mm)

(21.3mm)

A

O,1

ø1.97″ (50mm)

ø1.32″ ±.007 (33.5mm)

x

A

ø1.19″ ±.003

(30.1mm)

G1

1.20″ ±.003 (30.5mm)

O,1 A

0.59″ ±.007

(15mm)

0.81″ ±.012 (20.5mm)

0.59″ ±.007

(15mm)

0.41″ (10.5mm)

0.81″ ±.012

(20.5mm)

2-WIRE WIRING	3-WIRE WIRING

x

x

| + Supply | Red |
| --- | --- |
| + Output | Black |
| Ground | Gray |

| + Supply | Red |
| --- | --- |
| Common | Black |
| + Output | Brown |
| Ground | Gray |

85

623/624

Hazardous Location Pressure T ransmitters

Non-Incendive Pressure Transmitters

APPROVED

SERIES

- Vacuum and compound ranges through 0 psig to 15,000 psig; absolute ranges from 0 psia to 15 psia through 0 psia to 100 psia

- Current and voltage outputs available

- 316 Stainless Steel and Elgiloy wetted parts

- Factory Mutual and Canadian Standards Association approved

- CE compliant to suppress RFI, EMI and ESD

- NACE MR0175/ISO 15156 compliant

- NSI/ISA-12.27.01-2003 approved single seal

SPECIFICATIONS

APPLICATIONS

  - Chemical processing

  - Gas pressure measurement

  - Oil field & offshore

  - Mining

  - Well head measurement

NOSHOK 623 and 624 Series transmitters are Factory Mutual and Canadian Standards Association approved for use in hazardous location applications as follows:

Non-Incendive for: Class I, Division 2, Groups A, B, C and D.I.P; Class II, Division 1, Groups E, F and G Maximum ratings 30 Vdc, 20 mA.

CE compliant with pressure equipment directive 97/23EC. ANSI/ISA-12.27.01-2003, Approved single seal.

86

Output signals	4 mA to 20 mA, 2-wire; 1 Vdc to 5 Vdc low power, 3-wire; 0.5 Vdc to 4.5 Vdc low power, 3-wire

Pressure ranges	Vacuum through 0 psig to 15,000 psig

Absolute through 0 psia to 100 psia

Accuracy	±0.25% full scale (BFSL) (Includes the effects of non-linearity, hysteresis,

non-repeatability, zero point and full scale errors)

Stability	≤ ±0.2% full scale for 1 year, non-accumulating Response time	≤1 ms (between 10% and 90% full scale) Service life	>100,000,000 load cycles

Temperature ranges	Compensated 32 °F to 176 °F (0 °C to 80 °C)

Zero effect is ±0.011% full scale/ °F within compensated range Span effect is ±0.011% full scale/ °F within compensated range Media -40 °F to 212 °F (-40 to 100 °C)

Ambient -22 °F to 176 °F (-30 °C to 80 °C)

Storage -22 °F to 212 °F (-30 °C to 100 °C)

Power requirement*	10 Vdc to 30 Vdc (4 mA to 20 mA, 2-wire)

6 Vdc to 30 Vdc (1 Vdc to 5 Vdc, 3-wire, 0.5 Vdc to 4.5 Vdc, 3-wire)

14 Vdc to 30 Vdc (0 Vdc to 10 Vdc, 3-wire)

Load limitations	≤ (VPower -10)/0.020 Amp for 4 mA to 20 mA; ≥ 10,000 Ω for 1 Vdc to 5 Vdc, 3-wire

Proof pressure	3 times full scale for ranges 0 psi to 15 psi through 0 psi to 200 psi

1.75 times full scale for ranges 0 psi to 300 psi through 0 psi to 10,000 psi

1.5 times full scale for 0 psi to 15,000 psi range

Burst pressure	3.8 times full scale for ranges 0 psi to 15 psi through 0 psi to 200 psi

4 times full scale for ranges 0 psi to 300 psi through 0 psi to 10,000 psi 3 times full scale for 0 psi to 15,000 psi

Measuring element 623 Series is 316 Stainless Steel for ranges up through 0 psi to 300 psi, 316 Stainless Steel and Elgiloy for ranges 0 psig to 500 psig and higher; 624 Series is 316 Stainless Steel with NBR o-ring; FKM o-ring optional

Connection	316 Stainless Steel

Housing material	316 Stainless Steel

Environmental rating	IP65 to IP67 dependent upon electrical connection

Electromagnetic rating CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity, over-voltage and short circuit protected

Shock	1000 g’s according to IEC 60068-2-27

Vibration	20 g’s according to IEC 60068-2-6

Weight	Approximately 12 oz.

- Unregulated

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |
| --- | --- | --- | --- |
| SERIES | 623 Stainless Steel threaded connection |  | 624 316 Stainless Steel flush diaphragm * |
| PRESSURE RANGES | 30vac -30 inHg to 0 psig 30/30 -30 inHg to 30 psig 30/60 -30 inHg to 60 psig 30/100 -30 inHg to 100 psig 15 0 psig to 15 psig psig = gauge pressure psia = absolute pressure | 30 0 psig to 30 psig 60 0 psig to 60 psig 100 0 psig to 100 psig 200 0 psig to 200 psig 300 0 psig to 300 psig Other ranges available on request | 500 0 psig to 500 psig 6000 0 psig to 6,000 psig 1000 0 psig to 1,000 psig 8000 0 psig to 8,000 psig 1500 0 psig to 1,500 psig 10000 0 psig to 10,000 psig 2000 0 psig to 2,000 psig 15000 0 psig to 15,000 psig 3000 0 psig to 3,000 psig 15A 0 psia to 15 psia 5000 0 psig to 5,000 psig 100A 0 psia to 100 psia Note: 624 Series is available for pressure ranges up to 0 psig to 8,000 psig |
| ACCURACY | 1 ±0.25% full scale (BFSL) |  |  |
| OUTPUT SIGNALS | 1 4 mA to 20 mA, 2-wire | 3 1 Vdc to 5 Vdc, 3-wire, low power | 31 0.5 Vdc to 4.5 Vdc, 3-wire, low power |
| PROCESS CONNECTIONS | 2 1/4″ NPT male 8 1/2″ NPT male | 11 G 1/2 B ** 13 G 1 B (624 Series only, <30 psig) |  |
| ELECTRICAL CONNECTION 6 1/2″ NPT male conduit with 6' integral cable |  |  |  |
| OPTION | ST8 Threaded Orifice (623 Series only) |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

* Hastelloy flush diaphragm available upon request.

** 624 Series only, G 1/2 B Flush (≥ 30 psig).

EXAMPLE	623 – 500 – 1 – 1 – 8 – 6 – ST8

Series	623 Series

Pressure range	0 psig to 500 psig

Accuracy	±0.25% full scale (BFSL)

Output signal	4 mA to 20 mA, 2-wire

Process connection	1/2" NPT Male

Electrical connection	1/2" NPT Male conduit with 6' integral cable

Option	Threaded Orifice

0.70″

(18 mm)

Front flush process connections

For ranges 0 psi to 30 psi

0.59″ HEX

(15 mm)

0.75″

(19 mm)

through 0 psi to 8,000 psi

1.06″ (27mm)

For ranges 0 to 30 psi and below

O-ring 0.73″ x 0.94" x 0.08″

(18.5mmx 23.9mm)

0.39″

(10mm)	O-ring 0.59″ x 0.08″ (15mmx 2mm)

ø.71″ ±.003

(18mm)

G1/2 B

1.61″ (41mm)

1/2″ NPT

0.81″ (20.5mm)

0.81″ (20.5mm)

0.39″

(10mm)

ø1.18″ ±.003

(30mm)

G1 B

O-ring 1.17″ x 1.41″ x 0.08″ (29.7mmx 35.7mm)

O-ring 1.02″ x 0.08″ (26mmx 2mm)

2.75″

(70 mm)

Flush corresponding port weld-on adapters

ø.84″ ±.007

x

A

ø.72″ ±.007 (18.2mm)

G1/2

.76″ ±.003 (19.4mm)

(21.3mm)

A

O,1

ø1.97″ (50mm)	ø1.97″ (50mm)

G1

1.20″ ±.003 (30.5mm)

O,1 A

0.41″ (10.5mm)

0.41″ (10.5mm)

ø1.32″ ±.007 (33.5mm)

0.59″ ±.007

(15mm)

0.81″ ±.012 (20.5mm)

0.59″ ±.007

(15mm)

x

0.81″ ±.012

(20.5mm)

2-WIRE WIRING

  - ″ HEX

(27 mm) 1/2″ NPT

1.06″ (27 mm)

- WIRE WIRING

0.75″

(19 mm)

623/624 SERIES	INFORMATION

ORDERING

DIMENSIONS

x

x

| + Supply | Brown |
| --- | --- |
| + Output | Green |

| + Supply | Brown |
| --- | --- |
| Common | Green |
| + Output | White |

A

ø1.19″ ±.003

(30.1mm)

##### 87

Hazardous Location Pressure T ransmitters

Intrinsically Safe

APPROVED

###### APPLICATIONS

    - Chemical processing

    - Gas pressure measurement

    - Oil field & offshore

    - Mining

    - Vapory recovery systems

    - Well head measurement

NOSHOK 625 and 626 Series transmitters are Factory Mutual and Canadian Standards Association approved for use in hazardous location applications as follows:

Intrinsically Safe, entity approval for Class I, II and III, Division 1, Groups A, B, C, D, E, F and G; and Class I, Zone 0 Aex ia IIC Dust Ignition-proof for Class II and III, Division 2, Groups F and G Non-incendive for Class I, Division 2, Groups A, B, C and D.

CE compliant with pressure equipment directive 97/23EC. ANSI/ISA-12.27.01-2003, Approved single seal.

88

SERIES

625/626

Low pressure ranges for vapor recovery applications, vacuum and compound ranges through 0 psig to 15,000 psig;

absolute ranges from 0 psia to 15 psia through 0 psia to 300 psia

- Current output

- 316 and 14-4PH Stainless Steel wetted parts

- Factory Mutual and Canadian Standards Association approved

- CE compliant to suppress RFI, EMI and ESD

- NSI/ISA-12.27.01-2003 approved single seal

SPECIFICATIONS

Output signal	4 mA to 20 mA, 2-wire

Pressure ranges	Vacuum through 0 psig to 15,000 psig

Absolute from 0 psia to 15 psia through 0 psia to 300 psia

Accuracy	±0.25% full scale (BFSL); optional ±0.125% full scale (BFSL) (Includes the

effects of non-linearity, hysteresis, non-repeatability, zero point and full scale errors)

Stability	≤ ±0.2% full scale for 1 year, non-accumulating

Adjustment	± 10% full scale for zero and span Response time	≤ 1 ms (between 10% and 90% full scale) Service life	> 100,000,000 load cycles

Temperature ranges	Compensated 32 °F to 176 °F (0 °C to 80 °C)

Zero effect is ±0.011% full scale/ °F Span effect is ±0.011% full scale/ °F Media -4 °F to 185 °F (-20 °C to 85 °C)

Ambient -4 °F to 176 °F (-20 °C to 80 °C)

Storage -22 °F to 221 °F (-30 °C to 105 °C)

Power requirement*	10 Vdc to 30 Vdc (4 mA to 20 mA, 2-wire)

Load limitations	≤ (VPower-10)/0.020 Amp

Proof pressure	3.5 times full scale for ranges 0 psi to 5 psi through 0 psi to 200 psi

- times full scale for ranges 0 psi to 300 psi through 0 psi to 10,000 psi

1.5 times full scale for 0 psi to 15,000 psi

Burst pressure	4 times full scale for ranges 0 psi to 5 psi through 0 psi to 200 psi

4 times full scale for ranges 0 psi to 300 psi through 0 psi to 10,000 psi 3 times full scale for 0 psi to 15,000 psi

Measuring element	625 Series is 316 Stainless Steel for ranges up through 0 psi to 300 psi, 316 Stainless Steel with 17-4PH Stainless Steel for ≥300 psi;

626 Series is 316 Stainless Steel with NBR o-ring

Connection	316 Stainless Steel

Housing material	316 Stainless Steel

Environmental rating	IP65 to IP67 depending upon electrical connection

Electromagnetic rating CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity, over-voltage and short circuit protected

Shock	1,000 g’s according to IEC 60068-2-27

Vibration	20 g’s according to IEC 60068-2-6

Weight	Approximately 7 oz.

- Unregulated

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| SERIES | 625 Stainless Steel threaded connection 626 | 316 Stainless Steel flush diaphragm | 626H | Hastelloy flush diaphragm |
| PRESSURE RANGES | 4/12 oz/in2 -4 oz/in2 to 12 oz/in2 30/100 -30 inHg to 100 psig 150 12 oz/in2 0 oz/in2 to 12 oz/in2 30/150 -30 inHg to 150 psig 200 | 0 psig to 150 psig 5000 0 psig to 5,000 psig 100A 0 psia to 100 psia 0 psig to 200 psig 6000 0 psig to 6,000 psig 150A 0 psia to 150 psia 0 psig to 300 psig 7500 0 psig to 7,500 psig 200A 0 psia to 200 psia 0 psig to 500 psig 8000 0 psig to 8,000 psig 250A 0 psia to 250 psia 0 psig to 750 psig 10000 0 psig to 10,000 psig 0 psig to 1,000 psig 15000 0 psig to 15,000 psig 0 psig to 1,500 psig 15A 0 psia to 15 psia 0 psig to 2,000 psig 30A 0 psia to 30 psia 0 psig to 3,000 psig 60A 0 psia to 60 psia Note: 626 Series is available for pressure ranges up to 0 psig to 8,000 psig |  |  |
|  | 16 oz/in2 0 oz/in2 to 16 oz/in2 30/200 -30 inHg to 200 psig 300 |  |  |  |
|  | 50 inH2O 0 inH2O to 50 inH2O 3 0 psig to 3 psig 500 100 inH2O 0 inH2O to 100 inH2O 5 0 psig to 5 psig 750 30vac -30 inHg to 0 psig 15 0 psig to 15 psig 1000 |  |  |  |
|  | 30/15 -30 inHg to 15 psig 30 0 psig to 30 psig 1500 |  |  |  |
|  | 30/30 -30 inHg to 30 psig 60 0 psig to 60 psig 2000 |  |  |  |
|  | 30/60 -30 inHg to 60 psig 100 0 psig to 100 psig 3000 |  |  |  |
|  | psig = gauge pressure psia = absolute pressure Other ranges available on request |  |  |  |
| ACCURACY | 1 ±0.25% full scale (BFSL) 2 | ±0.125% full scale (BFSL) |  |  |
| OUTPUT SIGNAL | 1 4 mA to 20 mA, 2-wire |  |  |  |
| PROCESS CONNECTIONS | 2 1/4″ NPT male 13 8 1/2" NPT male 45 11 G 1/2 B * | G 1 B (626 Series only, <30 psig) SAE J514 FIG B |  |  |
| ELECTRICAL CONNECTIONS | 1 36″ cable (connected to option 8) 14 3 6-pin Bendix - IP65 25 8 Hirschmann (DIN EN 175301-803 Form A) 36 | Hirschmann connector 1/2 ″ NPT conduit - IP65 M12x1 (4-pin) IP67 Integral cable 36″ - IP67 |  |  |
| OPTION | ST8 Threaded Orifice (625 Series only) |  |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

* 626 Series only, G 1/2 B Flush (≥ 30 psig).

EXAMPLE	625 – 500 – 1 – 1 – 8 – 8 – ST8

eries sig FSL)

wire ale m A) ifice

1.85"

(

47 mm)

1.06" sq.

(27 mm)

1.10"

(28 mm)

1.65"

(42 mm)

1.06" sq.

(27 mm)

2.91"

(74 mm)

Hirschmann with 1/2″ NPT Female ISO 4400 conduit

1.06" HEX

(27 mm) 1/2" NPT

1.06"

(27 mm)

0.75"

(19 mm)

NOTE

See 621/622 Series for G1/2B and G1B Front Flush Process

Connection Dimensions pg. 85

Series	625 S

Pressure range	0 psig to 500 p

Accuracy	±0.25% full scale (B

Output signal	4 mA to 20 mA, 2-

Process connection	1/2" NPT M

Electrical connection	Hirschmann (DIN EN 175301-803 For

Option	Threaded Or

1.36″ (34.5 mm)

1.36″ (34.5 mm)

0.68"

(17.3 mm)

0.51"

(13 mm)

0.54"

(13.8 mm)

Integral 36″ cable

*6 pin Bendix

*M12 x 1 (4-pin)

*Note: mate supplied separately 2-WIRE WIRING

Hirschmann

625/626 SERIES	INFORMATION

ORDERING

DIMENSIONS

|  | Hirschmann | Cable | M12 | Bendix |
| --- | --- | --- | --- | --- |
| + Supply | 1 | Red/Brown | 1 | A |
| + Output | 2 | Black/Green | 3 | B |

89

Hazardous Location Level T ransmitters

Intrinsically Safe Submersible

APPLICATIONS

  - Irrigation

  - Tank monitoring

  - Water & wastewater

  - Well head measurement

NOSHOK 627 Series transmitters are Canadian Standards Association approved for use in hazardous location applications as follows:

Intrinsically Safe, entity approval for Class I, II and III, Division 1, Groups A, B, C, D, E, F and G; and Class I, Zone 0 Aex ia IIC

Dust ignition-proof for Class II and III, Division 1, Groups E, F and G Non-incendive for Class I, Division 2, Groups A, B, C and D

FMRC 3600, 3610, 3611, 3810 (including supplement #1),

ISA-S12.0. 01, IEC 60529 (including amendment #1).

CE compliant with pressure equipment directive 97/23EC.

90

SERIES

627

Ranges from 0 inH2O to 50 inH2O through 0 psig to 350 psig

- Current output

- 316 Stainless and 17-4PH Steel wetted parts

- Canadian Standards Association approved

- CE compliant to suppress RFI, EMI and ESD

SPECIFICATIONS

Output signal	4 mA to 20 mA, 2-wire

Pressure ranges	0 inH2O to 50 inH2O through 0 psig to 350 psig

Accuracy	±0.25 % full scale (BFSL); optional ±0.125% full scale (BFSL), for ranges

≥ 150 inH2O (Includes the effects of non-linearity, hysteresis, non-repeatability,

zero point and full scale errors)

Stability	≤ ±0.2% full scale for 1 year, non-accumulating Response time	≤1 ms (between 10% and 90% full scale) Service life	>100,000,000 load cycles

Temperature ranges	Compensated 32 °F to 122 °F (0 °C to 50 °C)

Zero effect is ±0.011% full scale/ °F within compensated range Span effect is ±0.011% full scale/ °F within compensated range Media 15 °F to 175 °F (-10 °C to 60 °C)

Ambient 15 °F to 122 °F (-10 °C to 50 °C)

Storage -30 °F to 175 °F (-34 °C to 60 °C)

Power requirement*	10 Vdc to 30 Vdc (4 mA to 20 mA, 2-wire)

Load limitations	≤ (VPower-10)/0.020 Amp-(0.043 Ω x length of cable in feet)

Proof pressure	2 times range

Burst pressure	3 times range

Measuring element	Diaphragm and cap: 316 Stainless Steel

17-4PH Stainless Steel for 0 psig to 350 psig Cable: Polyurethane, optional FEP

Connection	316 Stainless Steel

Housing material	316 Stainless Steel

Environmental rating	IP68

Electromagnetic rating CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity, over-voltage and short circuit protected

Weight	Approximately 7 oz. with standard nosecone - cable extra

* Unregulated

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| SERIES 627 |  |  |  |  |  |  |
| PRESSURE RANGES | 50inH2O 0 inH2O to 50 inH2O 100inH2O 0 inH2O to 100 inH2O 150inH2O 0 inH2O to 150 inH2O 250inH2O 0 inH2O to 250 inH2O 400inH2O 0 inH2O to 400 inH2O psig = gauge pressure inH2O = inches of water |  | 5 0 psig to 5 psig (11.5 ftH2O) 100 10 0 psig to 10 psig (23.1 ftH2O) 160 15 0 psig to 15 psig (34.6 ftH2O) 200 25 0 psig to 25 psig (57.7 ftH2O) 300 30 0 psig to 30 psig (69.2 ftH2O) 350 60 0 psig to 60 psig (138.4 ftH2O) ftH2O = feet of water Other ranges available on request. |  |  | 0 psig to 100 psig (230.7 ftH2O) 0 psig to 160 psig (369.1 ftH2O) 0 psig to 200 psig (461.3 ftH2O) 0 psig to 300 psig (692.3 ftH2O) 0 psig to 350 psig (807.3 ftH2O) |
| ACCURACIES | 1 | ±0.25% full scale (BFSL) |  | 2 | ±0.125% full scale (BFSL) on ≥ 150 inH2O |  |
| OUTPUT SIGNAL | 1 | 4 mA to 20 mA, 2-wire |  |  |  |  |
| PROCESS CONNECTIONS | N T | Stainless Steel nosecone G 1/2 B x 1/2″ NPT male with 1/4″ NPT female |  | W | Stainless Steel weighted nosecone (1.1 lb.) |  |
| ELECTRICAL CONNECTIONS | XX 38-XX | Standard Polyurethane cable Optional FEP cable | NOTE: XX = length of cable in feet |  |  |  |
| OPTIONS | CBC DC | Cable Clamp Desiccant Cartridge | FE JB |  | Filter Element Cable Junction Box |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

EXAMPLE	627 – 350 – 1 – 1 – N – 300

Series	627 Series

Pressure range	0 psig to 350 psig

Accuracy	±0.25% full scale (BFSL)

Output signal	4 mA to 20 mA, 2-wire

Process connection	Stainless Steel nosecone

Electrical connection	300' of submersible Polyurethane cable

Weighted Nosecone	NPT Adapter

0.20″ Dia (5 mm)

G1/2

1.06″

(27 mm)		    	  FKM o-ring

1.06″ HEX

(27 mm)

5.12″ (130 mm)

5.12″ (130 mm)

1/2″ NPT

1.81″

(46 mm)

Male	1/4″ NPT

Female

0.73″

(18.5 mm)

  - ″ Dia (5 mm)

  - WIRE WIRING

627 SERIES	INFORMATION

ORDERING

DIMENSIONS

| + Supply | Brown |
| --- | --- |
| + Output | Green |

1.06″ (26.92 mm)

##### 91

628

SERIES

    - Ranges from 0 psig to 5,000 psig through 0 psig to 20,000 psig

    - Current output

    - Inconel X-750 wetted parts

    - Canadian Standards Association approved

    - Every sensor comes with a Certificate of Calibration

    - Certifications pending:

      - Factory Mutual

      - ATEX

      - CE

###### APPLICATIONS

    - Acidizing

    - Choke & kill manifold

    - Fracturing & cementing

    - Mud logging & mud pumps

    - Oil field & offshore

    - Well head measurement

Shown with optional Electrical Connector Cage

SPECIFICATIONS

Output signal	4 mA to 20 mA, 2-wire

Pressure ranges	0 psig to 5,000 psig through 0 psig to 20,000 psig

Accuracy	±0.25% full scale (BFSL) (Includes the effects of non-linearity, hysteresis,

non-repeatability, zero point and full scale errors)

Stability	≤ ±0.2% full scale for 1 year, non-accumulating

Response time	< 2 m/s

Service life	> 10,000,000 load cycles

Temperature ranges	Compensated 40 °F to 140 °F (5 °C to 60 °C)

Zero effect is ±0.01% full scale/ °F Span effect is ±0.01% full scale/ °F

Media -40 °F to 185 °F (-40 °C to 85 °C)

Ambient -40 °F to 185 °F (-40 °C to 85 °C)

Storage -40 °F to 185 °F (-40 °C to 85 °C)

Power requirement*	10 Vdc to 28 Vdc

Load limitations	≤ (VPower-10)/0.020 Amp

Proof pressure	1.5 times full scale (22,500 psi maximum) Burst pressure	3 times full scale (22,500 psi maximum) Measuring element	Inconel X-750

Connection	Inconel X-750

Housing material	316 Stainless Steel

Environmental rating	IP67 depending upon electrical connection

Electromagnetic rating CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity, over-voltage and short circuit protected

Shock	100 g's according to IEC 60068-2-27

Vibration	15 g's according to IEC 60068-2-6

Hazardous Location Pressure T ransmitters

Intrinsically Safe Hammer Union

NOSHOK 628 Series transmitters are Canadian Standards Association approved for use in hazardous location applications as follows:

Intrinsically Safe Class I, DIV 1, Groups A,B,C,D,

-40°C,Tamb<+85°C T4, Class II, DIV 1, Groups E,F,G, Class III, Class I, Zone 0 AEx/Ex ic IIC T4.

Non-Incendive Class I, DIV 2, Groups A,B,C,D,

-40°C,Tamb<+85°C T4, Class II, DIV 2, Groups F,G, Class III, Class I, Zone 2 AEx/Ex ic IIC T4.

92

Weight	Approximately 6 lb.

* Unregulated

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SERIES 628 |  |  |  |  |  |  |  |  |  |
| PRESSURE RANGES | 5000 | 0 psig to 5,000 psig 6000 | 0 psig to 6,000 psig | 10000 | 0 psig to 10,000 psig | 15000 | 0 psig to 15,000 psig | 20000 | 0 psig to 20,000 psig |
| ACCURACY | 1 | ±0.25% full scale (BFSL) |  |  |  |  |  |  |  |
| OUTPUT SIGNAL | 1 | 4 mA to 20 mA, 2-wire |  |  |  |  |  |  |  |
| WIRING CODE (See Wiring Code Schematics below) | A C D | E F G |  | H * J |  |  |  |  |  |
| PROCESS CONNECTIONS | 14 | 2” Wing union (#1502) |  |  |  |  |  |  |  |
| ELECTRICAL CONNECTIONS | 3 36 | 6-pin Bendix (MIL-C-26482) Integral cable with gland |  | 44 | 4-pin (MIL-C-5015) |  |  |  |  |
| OPTION CH Carrying Handle EC Electrical Connector Cage |  |  |  |  |  |  |  |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

* H is the standard wiring code.

EXAMPLE

1.36″ (34.5 mm)

Series	628 Series

Pressure range	0 psig to 5,000 psig

Accuracy	±0.25% full scale

Output signal	4 mA to 20 mA, 2-wire

Wiring code	A

Process connection	2” wing union (#1502)

Electrical connection	..6-pin Bendix

Option	Carrying Handle

628 – 5000 – 1 – 1 A – 14 – 3 – CH

628 SERIES	INFORMATION

ORDERING

DIMENSIONS

WIRING CODE SCHEMATICS

| A | Pin A | + Supply | E | Pin A | + Supply | G | Pin B | + Supply | J | Pin A | + Supply |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Pin B | - Output |  | Pin B | - Output |  | Pin C | - Output |  | Pin B | - Output |
|  | Pin E | Ground |  | Pin E | + Shunt Cal |  | Pin D | Ground |  | Pin C | + Shunt Cal |
| C | Red | + Supply |  | Pin F | - Shunt Cal | H* | Pin A | + Supply |  | Pin D | - Shunt Cal |
|  | Black | - Output | F | Pin A | + Supply |  | Pin B | - Output |  | Pin E | SHIELD, NOT CONNECTED** |
| D | Red | + Supply |  | Pin B | - Output |  | Pin D | Ground |  | Pin F | SHIELD, NOT CONNECTED** |
|  | Black | - Output |  | Pin C | + Shunt Cal |  | Pin E | + Shunt Cal |  |  |  |
|  | White | - Shunt Cal |  | Pin D | - Shunt Cal |  | Pin F | - Shunt Cal |  |  |  |
|  | Green | Ground |  | Pin E | Ground |  |  |  |  |  |  |

* H is the standard wiring code.

** No internal connection to E or F.

3.84"

(97.5 mm)

0.97"

(24.6 mm)

3.69"

(93.7 mm)

Ø 2.88"    	 (73.2 mm)

4.08"	5.00"

(103.6 mm) (127 mm)

Optional Electrical Connector Cage

93

APPLICATIONS

    - Food & beverage processing

    - Pasteurization systems

    - Pharmaceutical

    - Medical

11 SERIES

##### Ranges from vacuum through 0 psig to 400 psig

- Current and voltage outputs available

- 316 Stainless Steel wetted parts

- Can be cleaned-in-place (CIP) or steamed-in-place (SIP)

- Meets 3A requirements for the food and beverage, dairy, pharmaceutical

and biotechnology industries

- ASME BPE compliant

- CE compliant to suppress RFI, EMI and ESD

SPECIFICATIONS

Output signals	4 mA to 20 mA 2-wire, 0 Vdc to 5 Vdc 3-wire, 1 Vdc to 5 Vdc 3-wire,

1 Vdc to 6 Vdc 3-wire, 0 Vdc to 10 Vdc, 3-wire, 1 Vdc to 11 Vdc 3-wire

Pressure ranges	Vacuum through 0 psig to 400 psig

Accuracy	±0.25% full scale (BFSL); Optional ±0.125% full scale (BFSL); (Includes the

effects of non-linearity, hysteresis, non-repeatability, zero point and full scale errors)

Stability	±0.2% full scale for 1 year, non-accumulating

Adjustment	±10% full scale for zero and span

Response time	< 10 ms

Service life	> 100,000,000 load cycles

Temperature ranges	Compensated 32 ºF to 175 ºF (0 ºC to 80 ºC)

Effect ±0.01%/ºF for zero and span Media -40 °F to 300 °F (-40 °C to 150 °C)

Ambient -40 ºF to 176 ºF (-40 ºC to 80 ºC)

Storage -40 °F to 212 °F (-40 °C to 100 °C)

Power requirement*	10 Vdc to 30 Vdc (4 mA to 20 mA, 2-wire, 0 Vdc to 5 Vdc, 3-wire, 1 Vdc to 5 Vdc, 3-wire, 1 Vdc to 6 Vdc, 3-wire)

14 Vdc to 30 Vdc (0 Vdc to 10 Vdc, 3-wire, Vdc to 11 Vdc, 3-wire)

Load limitations	≤ (VPower -10)/0.020 Amp for 4 mA to 20 mA output

≤ 5,000 Ω for 1 Vdc to 5 Vdc output

≤ 10,000 Ω for 0 Vdc to 10 Vdc output

≤ 4,500 Ω for 0.5 Vdc to 4.5 Vdc output

Proof pressure	3 times full scale for 0 psig to 2 psig through 0 psig to 200 psig

1.75 times full scale for 0 psig to 300 psig through 0 psig to 400 psig

Burst pressure	3.8 times full scale for 0 psig to 2 psig through 0 psig to 200 psig

4 times full scale for 0 psig to 300 psig through 0 psig to 400 psig

Measuring element	316 Stainless Steel

Connection	316 Stainless Steel

Housing material	316 Stainless Steel

Environmental rating	IP65

Electromagnetic rating CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Reverse polarity, overvoltage and short circuit protection

Shock	1,000 g’s according to IEC 60068-2-27

Vibration	15 g’s according to IEC 60068-2-6

Weight	Approximately 1.1 lb.

* Unregulated

Diaphragm seal must be installed facing downward or in a vertical position for drainability. Do not intall diaphragm seal facing in an upward position.

Sanitary Pressure T ransmitters

ASME-BPE Sanitary Clamp

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

94	California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| SERIES 110 |  |  |  |  |
| CLAMP SIZES | 12 | 1-1/2″ 16 2″ |  |  |
| SEAL FILL FLUID | 4 | FFL77 White oil Other food grade quality fill fluids available — please consult factory |  |  |
| TRANSDUCER | 615 | 615 Series transducer |  |  |
| ACCURACIES | 1 | ±0.25% full scale (BFSL) 2 ±0.125% full scale |  |  |
| PRESSURE | 01 | -30 inHg to 0 psig 16 -30 inHg to 150 psig 37 0 psig to 10 psig | 55 | 0 psig to 160 psig |
| RANGES | 04 | -30 inHg to 15 psig 19 -30 inHg to 200 psig 40 0 psig to 15 psig | 58 | 0 psig to 200 psig |
|  | 07 | -30 inHg to 30 psig 22 -30 inHg to 300 psig 43 0 psig to 30 psig | 61 | 0 psig to 300 psig |
|  | 10 | -30 inHg to 60 psig 31 0 psig to 100 inH2O 46 0 psig to 60 psig | 64 | 0 psig to 400 psig |
|  | 13 | -30 inHg to 100 psig 34 0 psig to 5 psig 49 0 psig to 100 psig |  |  |
| OUTPUT SIGNALS | 1 | 4 mA to 20 mA, 2-wire 3 1 Vdc to 5 Vdc, 3-wire 5 0 Vdc to 10 Vdc, 3-wire |  |  |
|  | 2 | 0 Vdc to 5 Vdc, 3-wire 4 1 Vdc to 6 Vdc, 3-wire 6 1 Vdc to 11 Vdc, 3-wire |  |  |
| ELECTRICAL | 1 | 36″ Cable attached to Hirschmann 14 Hirschmann connection with ISO 4400 1/2″ NPT conduit |  |  |
| CONNECTIONS | 3 | 6-pin Bendix 25 M12 X 1 (4-pin) |  |  |
|  | 8 | Hirschmann (DIN EN 175301-803 form A) 36 Integral 36″ cable |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

EXAMPLE	110 – 12 – 4 – 615 – 1 – 34 – 1 – 1

eries amp e oil eries FSL)

sig wire able

1.88"

(48 mm)

1.06" sq.

(27 mm)

1.10" sq.

(28 mm)

2.60"

(66 mm)

0.54"

(1	)

1.65"

(42 mm)

Integral cooling extension

3.8 mm

1.06" sq.

(27 mm)

0.750"

(19 mm)

0.116"

(2.95 mm)

Hirschmann with 1/2″ NPT Female ISO 4400 conduit

1.968"

(50 mm)

1-1/2" ASME-BPE

Sanitary Clamp

2.520"

(64 mm)

Series	11 S

Clamp size	.. 1-1/2" ASME-BPE Sanitary Cl

Seal fill fluid	FFL77 Whit

Transmitter	615 S

Accuracy	±0.25% full scale (B

Pressure range	0 psig to 5 p

Output signal	4 mA to 20 mA, 2-

Electrical connection	Hirschmann with 36" of c

1.36″ (34.5 mm)

1.36″ (34.5 mm)

0.68"

(17.3 mm)

0.51"

(13 mm)

Integral 36″

cable

*6 pin Bendix

*Note: mate supplied separately or customer supplied

- WIRE WIRING

*M12 x 1 (4-pin)

|  | Hirschmann | Cable | M12 | Bendix |
| --- | --- | --- | --- | --- |
| + Supply | 1 | Red | 1 | A |
| Common | 2 | Black | 3 | B |
| + Output | 3 | White | 4 | C |

WIRE WIRING

2" ASME-BPE

Sanitary Clamp

11 SERIES	INFORMATION

ORDERING

DIMENSIONS

|  | Hirschmann | Cable | M12 | Bendix |
| --- | --- | --- | --- | --- |
| + Supply | 1 | Red | 1 | A |
| + Output | 2 | Black | 3 | B |

##### 95

100 SERIES

##### Switch adjustment ranges from 15 psig to 30 psig through 15 psig to 150 psig

    - Standard Brass with NBR diaphragm wetted parts

    - 1 SPST N.O. or N.C. contact

N.C.

Switching parameters Number	1

SPECIFICATIONS

Pressure Switches

Mechanical Miniature Low Pressure

APPLICATIONS

- Hydraulics & pneumatics

- Pumps & compressors

- Tank monitoring

- Leak detection

- Water management

96

N.O.

Function	SPST N.O. or N.C. contact

Contact rating	Up to 42 Vdc 2A

Non-repeatability	5% of the adjusted value Contact material	Silver-plated, optional gold-plated Frequency	Max. 100 cycles/min

Pressure ranges	15 psig to 30 psig through 15 psig to 150 psig

Switch adjustment	Adjustment screw from 5 psig to 150 psig dependent on full scale range

Switch point	Full scale

Hysteresis	< 10% of the adjusted value

Service life	>1,000,000 load cycles

Temperature ranges	Media -13 °F to 185 °F (-25 °C to 85 °C)

Ambient -13 °F to 185 °F (-25 °C to 85 °C)

Storage -13 °F to 185 °F (-25 °C to 85 °C)

Proof pressure	Full scale

Measuring element	NBR diaphragm

1/8" NPT Male Brass

Housing material	Brass, optional Stainless Steel

Environmental rating	IP65

Weight	Approximately 0.07 lb

WARNING: This product can expose you to chemicals including Lead, which is known to the State of California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

100 SERIES	INFORMATION

ORDERING

DIMENSIONS

| ORDERING INFORMATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| SERIES 100 |  |  |  |  |
| SWITCH FUNCTIONS | 1 | 1 Normally open | 2 | 1 Normally closed |
| PROCESS CONNECTION | 1 | 1/8″ NPT male |  |  |
| SWITCH ADJUSTMENT RANGES | 5/30 | 5 psig to 30 psig | 15/150 | 15 psig to 150 psig |
| ELECTRICAL CONNECTION | 4 | 6.3 mm spade terminals |  |  |
| SWITCH POINT (if required) |  | Specify pressure |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

EXAMPLE	100 – 2 – 1 – 15/150 – 4 – 100

Series	100 Series

Switch function	1 normally closed

Process connection	1/8" NPT Male

Adjustable range	15 psig to 150 psig

Electrical connection	6.3 mm spade terminals

Switch point	100 psig

Switching Output Schematic

Normally Closed	Normally Open

P

P

0.91"

(23 mm)

0.38"

(9.8 mm)

0.91"

(23 mm)

X

1/8" NPT

0.35"

(9 mm)

" HE

(19 mm)

##### 97

200

SERIES

    - Switch adjustment ranges from 3 psig to 30 psig through 450 psig to 4,600 psig

    - Zinc-plated Steel with NBR diaphragm (< 225 psig); Steel piston with NBR seal (> 225 psig) wetted parts

    - SPDT single changeover contact configuration

    - RoHS compliant

Switching parameters Number	1

SPECIFICATIONS

APPLICATIONS

- Hydraulics & pneumatics

- Pumps & compressors

Function	SPDT, micro switch with silver-plated contacts,

gold plated contacts available on request

Contact rating	Up to 28 Vdc 2A Up to 50 Vac 4A

Non-repeatability	±2% of full scale adjustment range

Contact material	Silver-plated

Frequency	Max. 100 cycles/min

Media	Diaphragm type, compressed air or not corrosive liquids

Piston type, self lubricating fluids such as hydraulic oil or grease

Pressure ranges	3 psig to 30 psig through 450 psig to 4,600 psig

Diaphragm type: 870 psi max.; piston type: 5,000 psi max.

Pressure Switches

Mechanical Compact SPDT

Tank monitoring

- Leak detection

- Water management

98

Switch adjustment

Switch point	Full scale

Hysteresis

Diaphragm type, ≤ 10% of full scale adjustment range, minimum 100 psig,

Piston type, maximum 15% of full scale adjustment range

Service life	>1,000,000 load cycles

Temperature ranges	Media -4 °F to 176 °F (-20 °C to 80 °C)

Ambient -4 °F to 176 °F (-20 °C to 80 °C)

Storage -4 °F to 176 °F (-20 °C to 80 °C)

Proof pressure	870 psig or 5,000 psig depending on adjustment range

Measuring element	NBR diaphragm < 225 psig; Steel piston with NBR seal > 225 psig

1/4″ NPT zinc-plated Steel

Housing material	Zinc-plated Steel

Environmental rating

Spade terminals IP00 Cable connection IP67

Weight	Approximately 0.2 lb.

WARNING: This product can expose you to chemicals including Lead, which is known to the State of California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| SERIES 200 |  |  |  |  |
| SWITCH FUNCTION | 1 | Single changeover contact (SPDT) |  |  |
| PROCESS CONNECTION | 2 | 1/4″ NPT male |  |  |
| SWITCH ADJUSTMENT RANGES | 3/30 | 3 psig to 30 psig (870 psig) | 150/1700 | 150 psig to 1,700 psig (5,000 psig) |
| (Max. working pressure) | 7/115 | 7 psig to 115 psig (870 psig) | 150/2300 | 150 psig to 2,300 psig (5,000 psig) |
|  | 15/225 | 15 psig to 225 psig (870 psig) | 300/2900 | 300 psig to 2,900 psig (5,000 psig) |
|  | 150/425 | 150 psig to 425 psig (5,000 psig) | 300/3600 | 300 psig to 3,600 psig (5,000 psig) |
|  | 150/1150 | 150 psig to 1,150 psig (5,000 psig) | 450/4600 | 450 psig to 4,600 psig (5,000 psig) |
| ELECTRICAL CONNECTIONS | 4 | 6.3 mm Spade terminals | 36 | 18″ Integral cable |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

EXAMPLE	200 – 1 – 2 – 150/425 – 4

Series	200 Series

Switch function	Single changeover contact

Process connection	1/4" NPT Male

Adjustable range	150 psig to 425 psig

Electrical connection	6.3 mm spade terminals

4 mm adjustment

0.82"

(20.8 mm)

Switching Output Schematic

2

2.41"

(61.3 mm) 1.89"

(48 mm)

3

P

1

  - " (24 mm) HEX

0.47" (12 mm)

1/4" NPT

0.93"

(23.5 mm)

200 SERIES	INFORMATION

ORDERING

DIMENSIONS

##### 99

300

SERIES

    - Switch adjustment ranges from 3 psig to 30 psig through 450 psig to 4,600 psig

    - Standard zinc-plated Steel with NBR diaphragm (< 225 psig); Steel piston with NBR seal (> 225 psig) wetted parts

    - SPDT single changeover contact configuration

    - RoHS compliant

Switching parameters Number	1

SPECIFICATIONS

Pressure Switches

Mechanical Compact SPDT with Adjustable Hysteresis

APPLICATIONS

- Hydraulics & pneumatics

- Pumps & compressors

- Tank monitoring

- Leak detection

- Water management

100

Function	SPDT, micro switch

Contact rating	Up to 28 Vdc 2A Up to 125 Vac 4A Up to 250 Vac 4A

Non-repeatability	±2% of full scale adjustment range

Contact material	Silver-plated

Frequency	Max. 100 cycles/min

Media	Diaphragm type, compressed air or not corrosive liquids

Piston type, self lubricating fluids such as hydraulic oil or grease

Pressure ranges	3 psig to 30 psig through 450 psig to 4,600 psig

Diaphragm type: 870 psi max.; Piston type: 5,000 psi max.

Switch adjustment

Switch point	Full scale

Hysteresis	Adjustable, see charts below

Service life	>1,000,000 load cycles

Temperature ranges	Media -4 °F to 176 °F (-20 °C to 80 °C)

Ambient -4 °F to 176 °F (-20 °C to 80 °C)

Storage -4 °F to 176 °F (-20 °C to 80 °C)

Proof pressure	870 psig or 5,000 psig depending on adjustment range

Measuring element	NBR diaphragm < 225 psig; Steel piston with NBR seal > 225 psig

1/4″ NPT zinc-plated Steel standard connection, others available on request

Housing material	Zinc-plated Steel

Environmental rating	IP65

Weight	Approximately 0.2 lb.

WARNING: This product can expose you to chemicals including Lead, which is known to the State of California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| SERIES 300 |  |  |  |  |
| SWITCH FUNCTION | 1 | Single changeover contact, SPDT |  |  |
| PROCESS CONNECTION | 2 | 1/4″ NPT male |  |  |
| SWITCH ADJUSTMENT RANGES | 3/30 | 3 psig to 30 psig (870 psig) | 150/1700 | 150 psig to 1,700 psig (5,000 psig) |
| (Max. working pressure) | 7/115 | 7 psig to 115 psig (870 psig) | 150/2300 | 150 psig to 2,300 psig (5,000 psig) |
|  | 15/225 | 15 psig to 225 psig (870 psig) | 300/2900 | 300 psig to 2,900 psig (5,000 psig) |
|  | 150/425 | 150 psig to 425 psig (5,000 psig) | 300/3600 | 300 psig to 3,600 psig (5,000 psig) |
|  | 150/1150 | 150 psig to 1,150 psig (5,000 psig) | 450/4600 | 450 psig to 4,600 psig (5,000 psig) |
| ELECTRICAL CONNECTIONS | 1 | 36″ Cable (connected to option 8) | 8 | Hirschmann (DIN EN 175301-803 form A) |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

EXAMPLE	300 – 1 – 2 – 15/225 – 8

Series	300 Series

Switch function	Single changeover contact

Process connection	1/4" NPT Male

Adjustable range	15 psig to 225 psig

Electrical connection	Hirschmann

Additional Ordering Information Switch Set Point(s) (please specify)

1.85"

(47 mm)

1.06" sq.

(27 mm)

1.10"

(28 mm)

1.77"

(45 mm)

1.06" HEX

(27 mm)

0.47"

(12 m

1/4" NPT

1.06"

(27 mm)

1.35"

(34 mm)

Switching Output Schematic

2 / WHT

3 / RED

P

- / BLK

Switch Function

Hysteresis Function

300 SERIES	INFORMATION

ORDERING

DIMENSIONS

psi

psi

1

2

3

m)

##### 101

400

SERIES

- Switch adjustment ranges from 0 to 300 psig through 0 to 5,000 psig

- Standard zinc-plated Steel with NBR diaphragm (< 225 psig); Steel piston with NBR seal (> 225 psig) wetted parts

- SPDT single changeover contact configuration

- CE compliant to suppress RFI, EMI and ESD

Switching parameters Number	1

SPECIFICATIONS

APPLICATIONS

- Hydraulics & pneumatics

- Mobile hydraulics

- Power generation

- Pumps & compressors

Function	SPDT, micro switch

Contact rating	Up to 28 Vdc Max 4A Up to 250 Vac Max 3A

Non-repeatability	±2% of full scale of adjustment range Contact material	Silver-plated, self-cleaning Frequency	Max. 200 cycles/min.

Media	Diaphragm type, compressed air or non-corrosive liquids

Piston type, self-lubricating fluids such as hydraulic oil or grease

Pressure ranges	0 psig to 300 psig through 0 psig to 5,000 psig

Adjustment knob from 3 psig to 4,600 psig dependent on full scale range

Switch adjustment

Switch point	Full scale

Diaphragm type, 1% to 11% of adjustment range full scale

- Tank monitoring

Hysteresis

Piston type, 2% to 8% of adjustment range full scale

Pressure Switches

Mechanical Heavy-Duty

Water management

102

Service life	>1,000,000 load cycles

Temperature ranges	Media 14 °F to 176 °F (-10 °C to 80 °C)

Ambient 14 °F to 176 °F (-10 °C to 80 °C)

Storage 13 °F to 185 °F (-25 °C to 85 °C)

Proof pressure	300 psi or 5,000 psi depending on adjustment range

Measuring element	NBR diaphragm ≤ 230 psig

Stainless Steel piston with NBR seal ≥ 500 psig

1/4″ NPT and 7/16-20 SAE zinc-plated Steel connections standard, others

available on request

Housing material	Zinc-plated Steel

Environmental rating	IP65 for Hirschmann

IP67 for M12 x 1

Electromagnetic rating	CE compliant to EU Standard 73/23/EWG

RFI, EMI and ESD protection

Shock	30 g’s according to IEC 60068-2-27

Vibration	10 g’s according to IEC 60068-2-6

Weight	Approximately 0.66 lb.

WARNING: This product can expose you to chemicals including Lead, which is known to the State of California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| SERIES | 400 |  |  |  |
| SWITCH FUNCTION | 1 | Single Pole Double Throw (SPDT) |  |  |
| PROCESS CONNECTIONS * | 2 | 1/4″ NPT male | 19 | G 1/4 B female |
|  | 5 | 1/4″ NPT female | 45 | SAE J514 FIG B |
|  | 10 | G 1/4 B male |  |  |
| SWITCH ADJUSTMENT RANGES ** | 3/30 | 3 psig to 30 psig (300 psig) | 150/1700 | 150 psig to 1,700 psig (5,000 psig) |
| (Max. working pressure) | 7/115 | 7 psig to 115 psig (300 psig) | 150/2300 | 150 psig to 2,300 psig (5,000 psig) |
|  | 15/225 | 15 psig to 225 psig (300 psig) | 300/2900 | 300 psig to 2,900 psig (5,000 psig) |
|  | 150/425 | 150 psig to 425 psig (5,000 psig) | 300/3600 | 300 psig to 3,600 psig (5,000 psig) |
|  | 150/1150 | 150 psig to 1,150 psig (5,000 psig) | 450/4600 | 450 psig to 4,600 psig (5,000 psig) |
| ELECTRICAL CONNECTIONS | 1 | 36″ Cable (connected to option 8) | 8 | DIN EN 175301-803 Form A |
|  | 2 | M12 x 1 (4-pin) | 46 | Hirschmann with LED status indicator |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

- Note: Stainless Steel connection available, consult factory

** Please specify switch set point(s), rising or falling pressing, and switch hysteresis (if applicable)

EXAMPLE	400 – 1 – 2 – 3/30 – 8

Series	400 Series

Switch function	Single pole double throw

Process connection	1/4" NPT Male

Adjustable range	3 psig to 30 psig

Electrical connection	Hirschmann

1.18"

(30 mm)

Hirschmann

EN 175301-803

Form A

3.66"

(93 mm)

1.18"

(30 mm)

1.57"

(40 mm)

Switching Output Schematic

DIN

Hirschmann DIN 43650

M12 x 1

(4-pin)

Hirschmann DIN 43650

M12 x 1 (4-pin)

400 SERIES	INFORMATION

ORDERING

DIMENSIONS

1

2

3

4

1

3

2

103

500

SERIES

  - Vacuum ranges through 0 psig to 10,000 psig

  - Standard copper alloy wetted parts

  - Normally open (N.O.) or normally closed (N.C.) switching functions

  - CE compliant to suppress RFI, EMI and ESD

Switching parameters

Number	1 or 2

SPECIFICATIONS

Pressure Switches

Electronic Mag-Switch

APPLICATIONS

- HVAC

- Hydraulics & pneumatics

- Pumps and compressors

- Stamping & forming presses

- Transportation

104

Function	N.O. or N.C., p-switching

Contact rating	Max. 100 mA (max. 30 Vdc)

Non-repeatability	≤ 1% of full scale

Pressure ranges	Vacuum ranges through 0 psig to 10,000 psig

Switch adjustment

Switch point	Adjustment screw

Switching point    5 ...100% of full scale

Hysteresis	≤ 5% of full scale

Service life	>1,000,000 load cycles

Temperature ranges	Compensated 32° to 175 °F / 0° to 80 °C

Zero ± 0.06% full scale/ °F Span ± 0.06% full scale/ °F

Media -5° to 175 °F (-20° to 80 °C)

Ambient -5° to 175 °F (-20° to 80 °C)

Storage -22° to 175 °F (-30° to 80 °C)

| Power requirement* | 10 Vdc to 30 Vdc |  |
| --- | --- | --- |
| Proof pressure | 30 psi & lower 60 psi 150 psi & higher | 5x 4x 2x |

Measuring element	Copper alloy

316 SS > 600 psi

1/4″ NPT Brass connection standard

Housing material	Brass through 350 psi

Aluminum anodized 600 psi and higher

Environmental rating	IP67 for M12 x 1

Electromagnetic rating	CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Weight	0.2 lb. on ≤400 psi, 0.6 lb. on ≥600 psi

* Unregulated

WARNING: This product can expose you to chemicals including Lead, which is known to the State of California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

| ORDERING INFORMATION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SERIES 500 |  |  |  |  |  |  |  |  |
| SWITCH FUNCTIONS | 1 | 1 N.O. (PNP) | 2 | 1 N.C. (PNP) | 3 | 2 N.O. (PNP) | 4 | 2 N.C. (PNP) |
| PROCESS CONNECTIONS 1 1/8″ NPT male 2 1/4″ NPT male |  |  |  |  |  |  |  |  |
| PRESSURE RANGES | 30vac | -30 inHg to 0 psig | 100 | 0 psig to 100 psig | 750 | 0 psig to 750 psig | 5000 | 0 psig to 5,000 psig |
|  | 15 | 0 psig to 15 psig | 150 | 0 psig to 150 psig | 1000 | 0 psig to 1,000 psig | 7500 | 0 psig to 7,500 psig |
|  | 30 | 0 psig to 30 psig | 250 | 0 psig to 250 psig | 2000 | 0 psig to 2,000 psig |  |  |
|  | 60 | 0 psig to 60 psig | 350 | 0 psig to 350 psig | 3000 | 0 psig to 3,000 psig |  |  |
| ELECTRICAL CONNECTIONS | 2 | M12x1 (4-pin) |  |  |  |  |  |  |
| OPTIONS | BT8 Note: | Threaded Orifice M12 mating connectors & cord sets are available as separate options. |  |  |  |  |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

EXAMPLE	500 – 3 – 2 – 750 – 2 – BT8

Series	500 Series

Switch function	2 N.O. (PNP)

Process connection	1/4" NPT Male

Adjustable range	0 psig to 750 psig

Electrical connection	M12 x 1 (4-pin)

Option	Threaded Orifice

Additional Ordering Information Switch Set Point(s)

1.93"

(49 mm)

1.42"

(36 mm)

2.80"

(71 mm)

0.51"

(13 mm)

1/4" NPT

(please specify)

1.26"

(SW 32 mm)

1.87"

(47.4 mm)

1.25"

(31.8 mm)

2.38"

(60.4 mm)

Switching Output Schematic

P-switching output

1/4" NPT

0.51"

(13 mm)

400 psi & lower	600 psi & higher

| Function | Connector M12 x 1 (4-pin) |
| --- | --- |
| Power supply: + | 1 |
| Power supply: − | 3 |
| Switching output: S1 | 4 |
| Switching output: S2 | 2 |

P-switching

Wiring Diagrams

Connection table for M12x1 (4-pin) connector

500 SERIES	INFORMATION

ORDERING

DIMENSIONS

1 switching output	2 switching outputs

105

APPLICATIONS

- Hydraulics & pneumatics

- Power generation

- Pumps & compressors

- Stamping & forming presses

- Water & wastewater

SERIES

800

Compound and standard ranges from 0 psig to 10 psig through 0 psig to 7,500 psig

- 316L Stainless steel wetted parts

- Current and voltage outputs available

- 7 different output configurations available

- Display and electrical connection can be rotated independently

- CE compliant to suppress RFI, EMI and ESD

- RoHS compliant

SPECIFICATIONS

Pressure ranges

Compound and standard ranges from 0 psig to 10 psig through

0 psig to 7,500 psig

Switching parameters	Individually adjustable via external control keys

Number	1 or 2 (PNP or NPN)

Function	N.O., N.C., window, hysteresis (freely adjustable)

Contact rating	250 mA max.

Response time	≤5 ms

Accuracy	≤ 0.5 % of span

Switch point	.25 to 100% of full scale

Hysteresis	Fully adjustable

Transmitter parameters

Output signal	4 mA to 20 mA or 0 Vdc to 10 Vdc; programmable and freely adjustable Accuracy	≤±0.5% of span including non-linearity, hysteresis, zero offset and end value

deviation (corresponds to measured error per IEC 61298-2)

Non-repeatability	< 0.1% of span (IEC 61298-2)

Adjustment	Freely scalable within the range of 5:1

Service life	100,000,000 load cycles

Temperature ranges	Compensated 32 °F to 176 °F (0 °C to 80 °C)

Media -4 °F to 185 °F (-20 °C to 185 °C)

Ambient -4 °F to 176 °F (-20 °C to 80 °C)

Storage -4 °F to 158 °F (-20 °C to 70 °C)

Display	14 segment-LED, red 4-digit, height 0.35”

Power requirement*	15 - 35 Vdc

Max. 45 mA for versions without 4-20 mA output signal,

Pressure Switches

Electronic Indicating Transmitter/Switch

Current consumption	Max. 70 mA for versions with 4-20 mA output signal,

Total consumtpion max. 600 mA including switching current

Proof pressure	2 times full scale

Measuring element	<150 psi: 316L Stainless steel

≥150 psi: 316L, PH grade Stainless steel

Housing material	304 Stainless steel

Connection	316 stainless steel

Environmental rating	IP65 and IP67 per IEC 60529

Electromagnetic rating	CE compliant to EMC norm EN 61326:1997/A1:1998

RFI, EMI and ESD protection

Electrical protection	Protected against reverse polarity, over-voltage and short circuit

Shock	> 50 g’s according to IEC 60068-2-27

Vibration	> 20 g’s according to IEC 60068-2-6

Weight	Approx 0.49 lb.

* Unregulated

##### 106

| ORDERING INFORMATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| SERIES | 800 | 304 Stainless steel housing |  |  |
| SWITCH FUNCTIONS | 1 2 3 4 | 2 N.O. or N.C. (PNP or NPN) 1 N.O. or N.C. (PNP or NPN) with 4 mA to 20 mA 3-wire analog output - N.O. or N.C. (PNP or NPN) with 0 Vdc to 10 Vdc 3-wire output - N.O. or N.C. (PNP or NPN) with 4 mA to 20 mA analog output * | 5 6 7 | 2 N.O. or N.C. switch (PNP/NPN) with 0 Vdc to 10 Vdc 3-wire output * - N.O. or N.C. switch (PNP/NPN) with 4 mA to 20 mA/0 Vdc to 10 Vdc 3-wire output 2 ** - N.O. or N.C. switch (PNP/NPN) with 4 mA to 20 mA/0 Vdc to 10 Vdc 3-wire output *, ** |
| PROCESS CONNECTIONS | 2 8 | 1/4″ NPT male 10 G 1/4 B male 1/2″ NPT male 11 G 1/2 B male | 45 | SAE J514 FIG B (Non-Adjustable) |
| ADJUSTABLE RANGES (Max. working pressure) | 14.5vac 14.5/15 14.5/30 14.5/50 14.5/100 14.5/160 14.5/200 14.5/300 10 | -14.5 psig to 0 psig 15 0 psig to 15 psig -14.5 psig to 15 psig 25 0 psig to 25 psig -14.5 psig to 30 psig 30 0 psig to 30 psig -14.5 psig to 50 psig 50 0 psig to 50 psig -14.5 psig to 100 psig 100 0 psig to 100 psig -14.5 psig to 160 psig 160 0 psig to 160 psig -14.5 psig to 200 psig 200 0 psig to 200 psig -14.5 psig to 300 psig 300 0 psig to 300 psig 0 psig to 10 psig 500 0 psig to 500 psig | 1000 1500 2000 3000 5000 7500 10A 15A 25A | 0 psig to 1,000 psig 30A 0 psia to 30 psia 0 psig to 1,500 psig 50A 0 psia to 50 psia 0 psig to 2,000 psig 100A 0 psia to 100 psia 0 psig to 3,000 psig 160A 0 psia to 160 psia 0 psig to 5,000 psig 200A 0 psia to 200 psia 0 psig to 7,500 psig 300A 0 psia to 300 psia 0 psia to 10 psia 0 psia to 15 psia 0 psia to 25 psia |
| ELECTRICAL CONNECTIONS 2 M12 x 1 (4-pin) 3 M12 x 1 (5-pin), 2 switch and analog output |  |  |  |  |
| OPTIONS | ST8 | Threaded Orifice |  |  |

Please consult your local NOSHOK Distributor or NOSHOK, Inc. for availability and delivery information.

* Available only with a M12 x 1 (5-pin) connector

** Can switch between 4 mA to 20 mA / 0 Vdc to 10 Vdc

EXAMPLE	800 – 1 – 2 – 160 – 2 – ST8

Series	800 Series

Switch function	2 N.O. or N.C. (PNP or NPN)

Process connection	1/4" NPT Male

Adjustable range	0 psig to 160 psig

Electrical connection	M12 x 1 (4-pin)

Option	Threaded Orifice

1 switching output (M12x1) with 4 mA to 20 mA signal† p-switching

1 switching output (M12x1) with 4 mA to 20 mA signal† n-switching

≈Ø1.50"

x 1

1.06" HEX

(27 mm)

1.16"

(29.5 mm)

1/4" NPT

Display rotates >300°

(38 mm)

2 switching output (M12x1)

1.42"

4	3

power supply

sig. output

1	2

S1 output

4	3

power supply

sig. output

1	2

S1 output

(36 mm)

2 switching output (M12x1)

M12

power supply

4	3

S2 output

1	2

S1 output

power supply

4	3

S2 output

1	2

S1 output

p-switching

2 switching output (M12x1) with 4 mA to 20 mA signal†

4	3

power supply

5

S2 output

1	2

S1 output

sig. output

p-switching

  - witching

- switching output (M12x1) with 4 mA to 20 mA signal† n-switching

2.83"

(72 mm)

1.02"

(26 mm)

.51"

power supply

4

S2 output

1

S1 output

sig. output

2

5

3

(13 mm)

Ø1.38"

(35 mm)

Electrical Connection rotates >300°

800 SERIES	INFORMATION

ORDERING

DIMENSIONS

† Also applies to 0 Vdc to 10 Vdc output

107

#### PISTON-TYPE SNUBBERS

##### Resist clogging and are self cleaning

    - Five different sized pistons included with each snubber to ensure the correct amount of snubbing for virtually every application

    - Available in Brass and 316 Stainless Steel in 1/4" NPT, 1/2” NPT or SAE J1926-3: 7/16-20

    - Weight approximately 0.2 lb. for 1/4" & 7/16", and approximately 0.4 lb. for 1/2"

Options & Accessories

Piston-Type Snubbers Specifications

| PART NO. | SIZE | MATERIAL | PRESSURE RATING |
| --- | --- | --- | --- |
| 1325 | 1/4″ NPT | Brass | 6,000 psi |
| 1335 | SAE J1926-3:7/16-20 | Brass | 5,000 psi |
| 1350 | 1/2″ NPT | Brass | 6,000 psi |
| 5025 | 1/4″ NPT | 316 Stainless Steel | 15,000 psi |
| 5035 | SAE J1926-3:7/16-20 | 316 Stainless Steel | 8,000 psi |
| 5050 | 1/2″ NPT | 316 Stainless Steel | 15,000 psi |

Piston-Type Snubbers

| DIMENSIONS |  | 1/4″ NPT | 1/2″ NPT | SAE J1926-3: 7/16-20 |
| --- | --- | --- | --- | --- |
| A | IN | 0.812 | 1.125 | 0.812 |
|  | MM | 20.6 | 28.6 | 20.6 |
| B | IN | 1.60 | 1.875 | 1.60 |
|  | MM | 40.6 | 47.6 | 40.6 |
| C | IN | 1.04 | 1.25 | 1.24 |
|  | MM | 26.4 | 31.8 | 31.5 |
| D | IN | 0.56 | 0.625 | 0.36 |
|  | MM | 14.2 | 15.9 | 9.1 |

All Pressure Measurement Instrumentation Options & Accessories

| PISTON | SUGGESTED USE |
| --- | --- |
| A, B* | Gases |
| B, C | Water |
| C, D | Light Oil |
| E | Heavy Oil |

* Snubber assembled and shipped with the B piston installed

##### 108

For products shown that are composed of Brass or Carbon Steel:

WARNING: This product can expose you to chemicals including Lead, which is known to the State of California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

For products shown that are composed of Stainless Steel:

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

#### SINTERED SNUBBERS

##### Cost effective solution to protect expensive instrumentation

- Increases gauge readability by smoothing out pressure surges, pulsations

and spikes

- 5 basic elements available for each snubber to accommodate specific

application needs

- Snubbing action achieved by utilizing a corrosion resistant 316 Stainless Steel sintered porous element

- Exotic materials or intermediate disc grades available

- Provides long service life with no moving parts to wear out

- Weight approximately 0.2 lb. for 1/4" & 7/16", and approximately 0.4 lb. for 1/2"

Options & Accessories

Sintered Snubbers Specifications

| PART NO. | SIZE | MATERIAL | PRESSURE RATING |
| --- | --- | --- | --- |
| 1125-X | 1/4″ NPT | Brass | 6,000 psi |
| 1135-X | SAE J1926-3:7/16-20 | Brass | 5,000 psi |
| 1150-X | 1/2″ NPT | Brass | 6,000 psi |
| 5125-X | 1/4″ NPT | 316 Stainless Steel | 15,000 psi |
| 5150-X | 1/2″ NPT | 316 Stainless Steel | 15,000 psi |

Note: The “X” in the part number denotes the Disc option (example: 1135-C).

See chart below for Disc options.

| DIMENSIONS |  | 1/4″ NPT | 1/2″ NPT | SAE J1926-3 :7/16-20 |
| --- | --- | --- | --- | --- |
| A | IN | 0.812 | 1.125 | 0.812 |
|  | MM | 20.6 | 28.6 | 20.6 |
| B | IN | 1.60 | 1.875 | 1.60 |
|  | MM | 40.6 | 47.6 | 40.6 |
| C | IN | 1.04 | 1.25 | 1.24 |
|  | MM | 26.4 | 31.8 | 31.5 |
| D | IN | 0.56 | 0.625 | 0.36 |
|  | MM | 14.2 | 15.9 | 9.1 |

Sintered Snubbers Replacement Disc Options

| DISC GRADE | PART NO. | AVERAGE AIR FLOW ESTIMATE | MICRON GRADE (reference) | SUGGESTED USE |
| --- | --- | --- | --- | --- |
| A | PD8-A-SS1 | 0.25 L/MIN @ 1 psi | 2 | Gases |
| B | PD8-B-SS1 | 0.63 L/MIN @ 1 psi | 10 | Gases, Water |
| C | PD8-C-SS1 | 1.46 L/MIN @ 1 psi | 20 | Water, Light Oil |
| D | PD8-D-SS1 | 2.79 L/MIN @ 1 psi | 40 | Light Oil |
| E | PD8-E-SS1 | 3.14 L/MIN @ 1 psi | 60 | Heavy Oil |

Sintered Snubbers

Sintered Snubbers Replacement Discs

109

PIGTAIL STEAM SYPHONS

- Protect the instrument from the damaging effects of high temperature steam

- Recommended for use in steam applications and systems that contain superheated vapor

- Available in 1/4" and 1/2" NPT sizes in welded Steel, welded 316 Stainless Steel

or seamless 316 Stainless Steel with ratings to 3,800 psi @ 850 ºF

| PART NO. | COIL STYLE | SIZE | MATERIAL |
| --- | --- | --- | --- |
| 1225 | 90° | 1/4″ NPT | Welded Steel, schedule 40 |
| 1250 |  | 1/2″ NPT | Welded Steel, schedule 80 |
| 2225 |  | 1/4″ NPT | Welded 316SS, schedule 40 |
| 2250 |  | 1/2″ NPT | Seamless 316SS, schedule 80 |
| 1025 | 180° | 1/4″ NPT | Welded Steel, schedule 40 |
| 1050 |  | 1/2″ NPT | Welded Steel, schedule 80 |
| 2025 |  | 1/4″ NPT | Welded 316SS, schedule 40 |
| 2050 |  | 1/2″ NPT | Seamless 316SS, schedule 80 |
| 1425 | 270° | 1/4″ NPT | Welded Steel, schedule 40 |
| 1450 |  | 1/2″ NPT | Welded Steel, schedule 80 |
| 2325 |  | 1/4″ NPT | Welded 316SS, schedule 40 |
| 2350 |  | 1/2″ NPT | Seamless 316SS, schedule 80 |
| 1525 | 360° | 1/4″ NPT | Welded Steel, schedule 40 |
| 1550 |  | 1/2″ NPT | Welded Steel, schedule 80 |
| 2525 |  | 1/4″ NPT | Welded 316SS, schedule 40 |
| 2550 |  | 1/2″ NPT | Seamless 316SS, schedule 80 |

Product Specifications

Pigtail Steam Syphons

All Pressure Measurement Instrumentation Options & Accessories

110

For products shown that are composed of Brass or Carbon Steel:

WARNING: This product can expose you to chemicals including Lead, which is known to the State of California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

For products shown that are composed of Stainless Steel:

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov

B

A

A

B

B

A

A

B

90° Syphon	180° Syphon	270° Syphon	360° Syphon

| CONNECTION SIZE |  |  | 1/4″ NPT | 1/2″ NPT |
| --- | --- | --- | --- | --- |
| 90° | A | IN MM | 4.25 107.95 | 6.5 165.1 |
|  | B | IN MM | 2.625 66.675 | 4.0 101.6 |
| 180° | A | IN MM | 5.5 139.7 | 8.875 225.425 |
|  | B | IN MM | 2.5 63.5 | 4.0 101.6 |
| 270° | A | IN MM | 4.5 114.3 | 7.5 190.5 |
|  | B | IN MM | 2.625 66.675 | 4.0 101.6 |
| 360° | A | IN MM | 7.25 184.15 | 12.0 304.8 |
|  | B | IN MM | 2.625 66.675 | 4.125 104.775 |

SWIVEL ADAPTORS

- Temperature ratings: 15,000 psi @ 200 °F and 3,000 psi @ 1,000 °F

1/4" HEX STOCK

3-1/8" (79.4 mm)

A

Used with gauges and gauge valves to adjust the line of sight

- Rotates 360° to allow the connected instrument to be positioned in the desired direction

- The pressure connection is achieved with a tapered cone style compression fitting simply by tightening the swivel hex nut

- All 316 Stainless Steel construction

- Standard with 1/2" NPT male process – 1/2" NPT female instrument connections

- Also available with 1/4" NPT connections, same specifications apply

- Weight approximately 0.8 lb.

1/2" NPT

WARNING: This product can expose you to chemicals including Chromium (VI) and Nickel, which are known to the State of

California to cause cancer and birth defects or other reproductive harm. For more information go to www.P65Warnings.ca.gov 111

#### Gauge Configurations for High Temperature  Applications

##### 140 °F is the maximum recommended ambient media temperature for NOSHOK pressure gauges with Brass wetted parts, and 212 °F for gauges with Stainless Steel wetted parts. For applications in which media reaches temperatures above 212 °F, NOSHOK offers several accessories designed to prevent damage to the gauge, and maintain maximum performance and accuracy.

Recommended gauge configurations are listed below. Please note that these guidelines are intended to be general recommendations. Many conditions may affect the amount of temperature reduction; including ambient temperature, media type, and process configuration.

- Up to 140 °F: All NOSHOK pressure gauges will provide peak performance in this range

- Up to 212 °F: A gauge with Stainless Steel wetted parts is required, such as the NOSHOK 400 and

740 Series. Do NOT use a gauge with Brass wetted parts.

- Up to 287 °F: Accessories must be used to maintain gauge integrity and accuracy. Options include:

  - Pigtail Steam Syphon: For use with a Stainless Steel wetted parts gauge. Should be used in steam applications and systems that contain superheated vapor. The pigtail buffers the instrument from the damaging effects of high temperature steam by holding system fluid in the coil to provide a steam trap for the fluid to condensate and dissipate the heat. Reduces temperature by 75° F/ft. on average. Multiple configurations are available.

  - Armored Capillary Tube: For use with a Stainless Steel wetted parts gauge. Average temperature reduction is 75 °F/ft. Two feet of capillary tube can increase the media temperature range to 362 °F. Standard length is five feet, provided with thread connections; other lengths available on request. Gauge must be separated from the process with a mounting bracket or flange, and the extra capillary length can be rolled up if necessary. Recommended for use with clean media or gases.

  - Long Pipe: 1/2″ in diameter or greater in either Steel or Stainless Steel construction with a Stainless Steel wetted parts gauge. Average temperature reduction is 75 °F/ft. Pipes can be cut and threaded for custom applications.

  - Cooling Element: For use with a Stainless Steel wetted parts gauge. Average temperature reduction is 75 °F/4″ element. Use with other accessories for additional temperature decrease (long pipe, syphon, diaphragm seal).

  - Cooling Tower: For use with a Stainless Steel wetted parts gauge. Approved usage up to

temperatures of 312 °F. Average temperature reduction is 100 °F/8″ cooling tower.

Recommended for use with clean media or gases.

- Up to 300 °F: A high temperature system fill is required, such as silicone D.C 550, and a diaphragm

seal is recommended on a Stainless Steel wetted parts gauge.

For more information, contact NOSHOK at 440.243.0888

112

Process Conditions That Affect Pressure Gauge Accuracy & Performance

The technology used in today’s pressure gauges has been around since the mid-eighteen hundreds, and the pressure gauge is still one of the most common methods of measuring pressure today. The majority of pressure gauges today still incorporate the Bourdon tube, socket, and geared movement; along with a pointer and dial to indicate process pressure.

Since the pressure gauge is a purely mechanical device, attention to three process conditions is necessary. The three factors that can adversely affect accuracy and performance are Temperature, Vibration and Pulsation.

Temperature Influence:

For every 18 °F (10 °C) shift in temperature from which the gauge is calibrated, the user can experience up to a ±0.4% additional error. The cause is the change in the elasticity or spring rate of the Bourdon tube element with temperature. While it is difficult to circumvent the influence of ambient temperature, we can address the influence of process temperature. In steam service, the common practice is to install coil syphons or pigtail syphons to dissipate process heat. Another common practice is to install a diaphragm seal with capillary to separate the gauge from the high heat source. There are many options available with fill fluid in the seal and capillary system to withstand temperatures up to 600 °F. In severe cold ambient conditions, many users elect to heat trace their instrumentation via electric or steam trace. Process and ambient temperature is an important consideration when selecting and applying pressure gauges.

Vibration Influence:

Vibration due to pumps, motors, and other rotating equipment can cause excess wear and possible premature failure of internal working parts of a pressure gauge, which include the Bourdon tube and the movement or gear mechanism. Vibration also causes difficulty in accurate reading of the gauge, due to pointer oscillation. One of the most common causes of pressure gauge failure is exposure to continuous vibration. The most widely accepted remedy is to utilize a liquid filled pressure gauge. The fill fluid of choice is either Glycerin or Silicone. Liquid filled gauges address not only pointer oscillation, but also serve to protect and lubricate the internal geared movement.

Pulsation Influence:

Process pulsation can occur around the discharge of pumps as well as quick operating valves. Many users assume that liquid filling a pressure gauge will fully address pulsation. Although a liquid filled gauge helps to dampen the effects of pulsation, it often does not fully address this process condition. Pulsation dampeners are installed upstream of the gauge socket and they can be a piston-type snubber, a sintered

metal snubber, or a threaded in-flow restrictor in the socket of the gauge. A needle valve installed upstream

of the gauge that is "pinched down" or slightly opened, is another common practice to address pulsation. It is not recommended to rely solely on a needle valve to address pulsation, due to the fact that the user could inadvertently open the valve, and thereby negate flow restriction.  In clean fluids (gases or clean low viscosity liquids) a threaded orifice/flow restrictor or a sintered metal snubber is the least costly way to address pulsation. In dirtier and higher viscosity fluids a piston snubber is usually installed.

Summary:

Temperature, vibration and pulsation are three process conditions that adversely affect a pressure gauge. Being aware of these three process conditions, and taking the necessary steps to address them, can help minimize accuracy errors and add to the service life of the pressure gauge.

113

NOSHOK  Reference Guide

NOSHOK Transducer and Transmitter Pressure Sensing Technologies

Diffused Silicon Semiconductor Strain Gauge Sensor (used in 100, 200, 612, 613, 615, 616, 621, 622, 623, 624, 625, 626, 627,

640 and 650 Series - ranges up to 0 psi to 300 psi)

semiconductor sensor

diffused silicon strain gauge sensor element

sensor support

intermediate ring

supply voltage

diffused silicon strain gauge as a resistor

R1

R2

R3

R4

output to the amplifier

strain gauges diffused into silicon chip

silicone oil

P

Stainless Steel diaphragm

wheatstone bridge

Sputtered Thin Film Strain Gauge Sensor (used in 100, 200, 612, 613, 615, 616, 621, 622, 623, 624, 625, 626, 627, 640, 650, 660, 800/810 Series - ranges 0 psi to 500 psi and higher)

compression force on strain gauge

tension force on strain gauges

P

compression

force on strain gauge

passivation

P

wire bond

strain gauge

glass insulation

Stainless Steel body

supply voltage

R1	R2

R3	R4

wheatstone bridge

thin film strain gauge as a resistor

output to the amplifier

R1

R2

R3

R4

Ceramic Thick Film Strain Gauge Sensor (used in 800/810 and 1000 Series)

thick

o-rin

pressure connection

P

tension ring

thick film strain gauge as a resistor

glass

P

ceramic diaphragm

strain gauges	ceramic body

film cell g

supply voltage

output to the amplifier

wheatstone bridge

hall effect element

ceramic magnet

hall effect element

Hall Effect Sensor

ceramic magnet

input current

output to the amplifier

pressure sensitive

diaphragm	P

magnetic current

##### 114

NOSHOK Accuracy Specifications

full scale error

zero point error

pressure

signal

Accuracy	according to IEC 61298-2

Non-linearity	according to IEC 61298-2

Definitions

Characteristic Curves:

A smooth curve generated through data points recorded from actual input pressures and output signals

at increasing and decreasing pressures (upscale and downscale readings)

Ideal Characteristic Line :

A straight line representing an ideal linear relationship between

the input pressure and output signal.

Hysteresis:

The maximum dif ference between the characteristic lines recorded at increasing and decreasing pressure. Expressed in percent of ideal span.

Accuracy :

The maximum deviation from an ideal characteristic line including the ef fects of non-linearity , hysteresis, non-repeatability, zero point and full scale errors. Expressed in percent of ideal span

Non-Repeatability :

The maximum deviation between values

of output for any single input of multiple cycles considering decreasing and increasing pressures separately.

Expressed in percent of ideal span.

pressure

Averaged Characteristic Curve:

A single curve generated through the averaged data of input pressures and output

signals at increasing and decreasing pressures. (average of upscale and downscale curves)

Reference line (TP or BFSL):

signal

A straight line coinciding with the actual output data and the averaged characteristic curve.

(TP)Terminal Point connects the actual zero point value and the full scale value (BFSL) Best Fit Straight Line connects the data using the least square method

to minimize the maximum deviation

TP	2 X BFSL

Non-Linearity:

The maximum deviation from the averaged characteristic line to the the reference line.

Expressed in percent of ideal span.

115

Thermal Performance of NOSHOK Pressure Transducers

Temperature Performance 100 Series Pressure Transmitter

The above diagram illustrates transducer performance related to the temperature of the environment and media being measured.

The graph shows the worst case performance of the series 100 pressure transmitter as an example (other series follow the same pattern). The thermal specification as indicated in the 100 series specifications is given in a worst case coefficient for the combined effects on zero and span. The definitions are as follows.

The Compensated Temperature Range is the thermal band over which the effect specification is guaranteed. For the 100 series, the coefficient is +/-0.0167% full scale per °F. This means that over the compensated temperature range the thermal boundaries are straight lines as shown. This is sometimes called a “bow-tie effect” or “butterfly effect”.

The Ambient Temperature Range is the maximum and minimum ratings over which the transducer will output a correct signal.

The Media Temperature Range is the maximum and minimum ratings of the media at the process connection. The Storage Temperature Range is the maximum and minimum ratings for no damage on the shelf.

##### 116

The Minimum Power Supply Voltage Required For A 2-Wire 4 mA to 20 mA Loop

Single instrument 2 wire current loop	Single instrument 2 wire current loop

For the single instrument 2 wire current loop, the minimum power supply voltage is equal to the required voltage across the

transmitter plus the voltage drop across the instrumentation plus the voltage drop caused by the resistance of the wiring.

As an example, for a 100 series (4 mA to 20 mA output) pressure transmitter, Vtransmitter = 10 Vdc

Vwiring = Resistance of the wiring (handbook data) X 20 mA maximum current flow in the circuit. If the instrumentation has an input resistance of 250 Ω and if the resistance of the wiring is minimal (100 ft of 24 AWG leadwire has less than 0. 6 Ω (negligible) of resistance), then the calculation including the leadwire is as follows:

Vmin = 10 Vdc + (250 Ω) x .020 Amp + (0.6 Ω) x .020 Amp = 15.012 Vdc

The power supply must provide at least this voltage with the current consumption of .020 Amp.

In a multiple instrument 2 wire current loop, if the second instrument also has an input resistance of 250 Ω, then a second component on the right side of the equation must be included. In this case, the Vmin= 20.012 Vdc. A power supply of 24 Vdc, 1 Amp would be a typical choice.

Load Limitations 4 mA to 20 mA output

If there is more than 1 transmitter loop operating off of the same power supply then the current (.020 Amp) must be multiplied by the number of loops. It is recommended that the power supply provide 20% to 30% higher excitation voltage than that calculated above.

Vmin = 10V + (.020 x RL)

RL = Loop resistance (Ω) RL = RS + RW

RS = Sensor resistance (Ω) RW = Wire Resistance (Ω)

117

Measuring The Pressure Of High Temperature  Media

In many applications the medium that the transducer or transmitter will contact may be at an elevated temperature beyond the operational limit of the measuring instrument. Selecting an instrument with a high temperature rating or using diaphragm seals to provide isolation from the medium may not be feasible from a design or economic standpoint.

One way to address this situation is to mount the instrument with a short length of tubing away from the hot area where the measurement needs to be made. With a dead ended pressure chamber, the tubing will effectively dissipate much of the heat and bring the medium in contact with the measuring instrument down to a lower temperature that

is within its safe and accurate limit.

The following chart provides the basic information needed to determine the size and material of the tubing needed.

These curves are based upon the following assumptions:

- The pressure vessel is insulated to limit radiant heat transfer to the transducer – the major source of thermal input is via the connecting tube.

- The pressure medium has a coefficient of thermal conductivity less than .4btu / hr / ft2 / ft / °F. This figure encompasses a wide range of liquids and gases.

- The ambient temperature TA around the transducer is 100 °F.

- The heat transfer rate (convection) from the tubing to still air is 1.44btu / ft2 / hr / °F.

118

Environmental Ratings	                                                                             IP Environmental Protection Codes

First Numeral - Protection from Particles	Second Numeral - Protection from Water

- No protection	0 No protection

- Particles >50 mm	1 Vertical falling water

- Particles >12 mm	2   Direct sprays up to 15° from vertical

- Particles >2.5 mm	3   Direct sprays up to 60° from vertical

- Particles >1 mm	4 Direct sprays from all directions - limited ingress permitted

- Dust protected - limited ingress, no deposits	5 Low pressure jets of water from all directions - limited ingress permitted	6 Strong jets of water from all directions

- Dust tight - totally protected	7   Immersion in water from 15 cm to 1 m

8 Immersion in water under pressure for long periods of time IP (first numeral, second numeral), for	9 High pressure steam jet up to 100 bar

example IP67

Environmental ratings on NOSHOK transducers are indicated with the individual specifications throughout this catalog. The following ratings are used and this is how they are defined.

IP65	Totally protected from dust as well as protection from low pressure jets of water from all directions - limited ingress permitted (no effect on performance)

IP67	Dust tight and capable of immersion in water from 15 cm to 1 m

IP68	Capable of immersion in water for long periods of time.

IP69K	Capable of steam jet washdown.

Since IP65, NEMA 4 and NEMA 4X are related, the differences are in the standards used in qualification. Here they are:

|  | IP65 | NEMA 4 |
| --- | --- | --- |
| Method | Stream of water | Stream of water |
| Nozzle Size | 1/2 ″ | 1 ″ |
| Distance | 10 ft | 10 ft |
| Duration | 15 minutes | 5 minutes |
| Direction | All angles | All angles |
| Pressure/Flow | 10 m of water | 65 gallons/min. |

In order to meet the standard, the IP65 test results allow some ingress of water as long as it does not affect the performance of the instrument. In order to meet the standard, the NEMA 4 test results do not allow any ingress of water. NEMA 4X includes the NEMA 4 standard requirements plus corrosion resistance.

119

Hazardous Location Classifications (NEC)

Class I:	Areas in which flammable gases or vapors may be present in the air in sufficient quantities to be explosive

Group A: Atmospheres containing acetylene

##### Group B: Atmospheres such as butadiene, ethylene oxide, propylene oxide, acrolein, or hydrogen (gases or vapors

equivalent in hazard to hydrogen,such as manufactured gas)

Group C: Atmospheres such as cyclopropane, ethyl ether, ethylene, gas or vapors of equivalent hazard

Group D: Atmospheres such as acetone, alcohol, ammonia, benzene, benzol, butane, gasoline, hexane, lacquer solvent vapors, naphtha, natural gas, propane, or gas or vapors of equivalent hazard

Class II:	Areas made hazardous by the presence of combustible dust

Group E:	Atmospheres containing combustible metal dusts, regardless of resistivity; dust of similarly hazardous

characteristics having a resistivity of less than 100 KΩs-cm; electrically conductive dusts

Group F:	Atmospheres containing combustible carbon black, charcoal, or coke dusts having more than 8% total volatile material; dusts so sensitized that they present an explosion hazard, and dusts having a resistivity of greater than 100 Ω-cm but less than or equal to 1x108 Ω-cm

Group G: Atmospheres containing combustible dust having resistivity equal to or greater than 100K Ω-cm; electrically

nonconductive dusts

Class III:	Areas made hazardous by the presence of easily ignitable fibers or dust, but which are not likely to be in suspension in the air in quantities that are sufficient to ignite

Division 1: Atmospheres where hazardous concentrations exist continuously, intermittently or periodically under normal operating conditions

Division 2: Atmospheres where hazardous concentrations exist only in case of accidental rupture or breakdown of

equipment

Hazardous Location Pressure Measurement with NOSHOK Pressure Transmitters

NOSHOK has solutions to your applications in areas with flammable gases and liquids. Let’s start with the definitions related to equipment used in hazardous environments:

Intrinsic Safety Protection

Protection in which the measurement system contains only transmitters and associated equipment that are incapable of causing ignition of the surrounding flammable atmosphere. Normally an intrinsic safety barrier is employed between the transmitter which is located in the hazardous area and the downstream receiving equipment. This barrier contains a electrical network designed to limit the energy (voltage and current) available to the protected circuit in the hazardous location under specified fault conditions. NOSHOK 625, 626 and 627 Series are Factory Mutual and Canadian Standards Association approved as intrinsically safe.

Non-Incendive Protection

Protection in which the measurement may contain arcing or sparking equipment but is still incapable, under specified test conditions, of igniting the flammable gas, vapor or dust-air mixture. This applies only in Division 2 environments. An intrinsic safety barrier is not required in this measurement system. No special wiring is required. NOSHOK 623 and 624 Series are Factory Mutual and Canadian Standards Association approved as non-incendive.

Explosion-Proof Protection

Protection in which the enclosure of the transmitter is capable of withstanding an explosion of the specified gas or vapor that may occur within it and of preventing the ignition of a specified gas or vapor surrounding the enclosure by sparks, flashes or explosion of the gas or vapor within, and that operates at such an external temperature that a surrounding flammable atmosphere will not be ignited. Explosion-proof installation techniques are required including special electrical conduit and junction boxes. NOSHOK 621 and 622 Series are Factory Mutual approved as explosion-proof.

120

Why NOSHOK Is The Best Choice

  - Stable sensing technologies mean that there is no need for periodic recalibration. NOSHOK transducers do not have glues, epoxies or adhesives in the transduction portion of the sensor module because such organic agents cause calibration drift with temperature and pressure cycling, and over time in some applications, cause complete failure.

  - Broad product offering results in best fit of product configuration to customer application requirements.

  - CE compliance and an environmentally hardened design mean maximum performance and reliability in difficult real world

applications. Products are manufactured in an ISO 9001 certified facility.

  - All product specifications are conservatively stated in the literature so that product performance exceeds customer expectations.

  - No specsmanship or games are ever employed, only honest information.

  - The calibration of every product is verified in NOSHOK’s modern facility with the best available pressure controllers and

computerized readout equipment that are at least 4 times the accuracy of the product being checked.

  - Highly automated production minimizing the variations in product caused by human labor mean more consistency from unit to unit resulting in interchangeability and consistent performance.

  - Simple and proven dc electronics improves reliability and longer mean time between failure (MTBF) characteristics.

  - While field failures are few, NOSHOK backs it’s electronic products with a 3-year warranty that is the best in the market.

  - Products provide significant performance and application flexibility at competitive prices addressing the needs of the OEM and the user alike.

  - As a privately owned and run business, NOSHOK employees focus on continually improving customer satisfaction.

Specsmanship - What to Look for in Comparing Other Transducers and Transmitters to NOSHOK Products

  - Be on the lookout for suppliers specifying “high accuracy” with a low price. In many cases you will find indications of zero offsets and span offsets of up to 2% each. The specified accuracy of NOSHOK transducers includes any offsets and is a true accuracy upon which you can depend.

  - If the competitors do not specify a long term stability specification, then this bears out our contention that many of these

other sensing technologies do not yield an attractive stability specification otherwise it would be printed in the literature.

  - Look out for the “typical” nomenclature or the Root-Sum-Square (RSS) designation. While these methods provide a statistical probability of how most of the products will perform, it means that if a quantity of units is considered then a percentage of the products will not meet the listed specification. NOSHOK specifications are worst case, so all the transducers meet that specification.

121

NOSHOK Transmitters/Transducers Wiring Diagrams & Electrical Connections for 100, 200, 300, 612, 615/616, 640, 660 and 800 Series

Installation: NOSHOK pressure transmitters/transducers may be mounted in any plane with negligible effect on performance. Although these units are designed and manufactured to withstand substantial shock and vibration, it is recommended that they be mounted in an area of minimal vibration. Always use a wrench on the wrench flats when installing. NEVER use a pipe wrench on the housing or in the area of the electrical connection.

Maintenance/Calibration: NOSHOK pressure transmitters/transducers require no maintenance. Recalibration is dependent on the users Quality Assurance Program. If no program is in place, NOSHOK recommends a 1 year cycle.

Alignment Procedure

Using a pressure source and meter with adequate accuracy,

perform the following steps:

- Open sensor

- With no pressure applied,adjust the “Z”

SERIES 612 & 613

2 WIRE WIRING DIAGRAM EXAMPLE

Blue

Power

potentiometer for the correct Zero output

- Apply the correct full scale pressure to the unit

- Adjust the “S” potentiometer for the correct

SERIES 100

Span output

Span

Zero

Red

Supply

Black

Output

Wiring –

2 WIRE WIRING DIAGRAM EXAMPLE

Mini-Hirschmann connector

Load Limitations

4 mA to 20 mA Output Only

Vmin = [10V + (.020 x RL)] − 0.04352

+ Output

Output

Power Supply

cable length

Wiring –

M12 x 1 (4-pin) round connector

RL	= RS + RW

| Series 612 | 4 mA to 20 mA 2-wire |
| --- | --- |
| + Supply | Red |
| +Output | Black |
| Case ground | Blue |

RL	= Loop Resistance (Ωs) RS	= Sense Resistance (Ωs) RW	= Wire Resistance (Ωs)

Current output, 2 wire

+ Supply

Red

Black

Supply

Power

Output

1

3

2

Output	+ Output

2 WIRE

+ Supply		WIRING DIAGRAM EXAMPLE

Power Supply

Load Limitations

4 mA to 20 mA Output Only Vmin = 10V + (.020 x RL) RL	= RS + RW

RL	= Loop Resistance (Ωs) RS	= Sense Resistance (Ωs) RW	= Wire Resistance (Ωs)

| Series 100 | 4 mA to 20 mA 2-wire |
| --- | --- |
| + Supply | Red/1/A/1/Brown |
| +Output | Black/2/B/3/Blue |

Example: Red/1/A/1 = Applicable color wire/din plug number/Bendix pin/M12 x 1 pin number/M12 integral cable color wire

3 WIRE WIRING DIAGRAM EXAMPLE

SERIES 200

Wiring –

3 WIRE WIRING DIAGRAM EXAMPLE

Mini-Hirschmann connector

Voltage output, 3 wire

Power

Supply

+ Supply

1

Output

3 2

•

+ Output

Power Supply

Red

- Black

White

Red

Blue

White

Output

Black

•

Power Supply

Output

Wiring –

0-5, 1-6, -10

1 Vdc to 11 Vdc 3-WIRE

Series 200

M12 x 1 (4-pin) round connector

Common

+ Output

•

Power Supply

+ Supply

Output

Common

3 WIRE WIRING DIAGRAM EXAMPLE

Load Limitations

4 mA to 20 mA Output Only

Vmin = [10V + (.020 x RL)] − 0.04354

cable length

RL	= RS + RW

+ Supply

RL	= Loop Resistance (Ωs) RS	= Sense Resistance (Ωs) RW	= Wire Resistance (Ωs)

Red/1/A/1/Brown

White/3/C/4/Black

+Output

Black/2/B/3/Blue

Common

| Series 612 | Voltage Output |
| --- | --- |
| + Supply | Red |
| Common | Black |
| +Output | White |
| Case ground | Blue |

Example: Red/1/A/1 = Applicable color wire/din plug number/Bendix pin/ M12 x 1 pin number/M12 integral cable color wire

##### 122

SERIES 615/616

SERIES 640

Red

Black

Output

Power Supply

Load Limitations 4 mA to 20 mA Output Only

Vmin = 10V + (.020 x RL)

RL	= RS + RW

| Series 615/616 | 4 mA to 20 mA 2-wire |
| --- | --- |
| + Supply | Red/1/A/1/1/Brown |
| +Output | Black/2/B/2/3/Blue |

RL	= Loop Resistance (Ωs) RS	= Sense Resistance (Ωs) RW	= Wire Resistance (Ωs)

Wiring - M12 x 1 (4-pin)

Red

Power Supply

White

Output

- Black

round connector

Current output, 2 wire

+ Output

Output

Power Supply

+ Supply

Voltage output, 3 wire

+ Output

- Common

Output

Power Supply

+ Supply

| Series 615/616 | Voltage Output |
| --- | --- |
| + Supply | Red/1/A/1/1/Brown |
| Common | Black/2/B/2/3/Blue |
| +Output | White/3/C/3/4/Black |

| Power Supply | Red |  |
| --- | --- | --- |
|  |  | Black |

2 WIRE WIRING DIAGRAM EXAMPLE

Output

Example: Red/1/A/1/1 = Applicable color wire/ din plug number/Bendix pin/junction

box pin/M12 x 1 pin number/M12 integral cable color wire

SERIES 300

Load Limitations 4 mA to 20 mA Output Only

Vmin = 10V + (.020 x RL)

RL	= RS + RW

| Series 300 | 4 mA to 20 mA 2-wire |
| --- | --- |
| + Supply | Red/1/1/1/Brown |
| +Output | Black/2/2/3/Blue |

RL	= Loop Resistance (Ωs) RS	= Sense Resistance (Ωs) RW	= Wire Resistance (Ωs)

Power Supply

3 WIRE WIRING DIAGRAM EXAMPLE

- Black

Red

White

Output

Load Limitations

4 mA to 20 mA Output Only Vmin = 10V + (.020 x RL) RL	= RS + RW

RL	= Loop Resistance (Ωs) RS	= Sense Resistance (Ωs) RW	= Wire Resistance (Ωs)

RS 232 Interface

1	1

6

2	RX	2

7	RT

- TXD	3

8

- DT	4

9

- GND	5

Pressure Sensor

6

white

- brown yellow

- green

9

2 WIRE WIRING DIAGRAM EXAMPLE

| Series 300 | Voltage Output |
| --- | --- |
| + Supply | Red/1/A/1/1/Brown |
| Common | Black/2/2/3/Blue |
| +Output | White/3/3/4/Black |

Example: Red/1/1/1 = Applicable color wire/din plug number/junction box pin/

M12 x 1 pin number/M12 integral cable color wire

3 WIRE WIRING DIAGRAM EXAMPLE

SERIES 800

4 mA to 20 mA, 2 wire

+ Supply

Power

Supply

Output	+ Output

SERIES 660

0 Vdc to 10 Vdc, 3 wire

Wiring - Mini-Hirschmann connector

Current output, 2 wire

1

3

2

Output

+ Output

Power Supply

+ Supply

Load Limitations 4 mA to 20 mA Output Only

Vmin = 10V + (.020 x RL)

RL	= RS + RW

| Series 660 | 4 mA to 20 mA 2-wire |
| --- | --- |
| + Supply | Brown/1/1/Brown |
| +Output | Green/2/3/Blue |

RL	= Loop Resistance (Ωs) RS	= Sense Resistance (Ωs) RW	= Wire Resistance (Ωs)

Wiring - M12 x 1 (4-pin) round connector

Current output, 2 wire

+ Output

Output

Power Supply

+ Supply

- Common

+ Output

Output

Power

Supply

Load Limitations

+ Supply

Voltage output, 3 wire

1

3

2

- Common

+ Output

Output

Power Supply

+ Supply

| Series 660 | Voltage Output |
| --- | --- |
| + Supply | Brown/1/1/Brown |
| Common | Green/2/3/Blue |
| +Output | White/3/4/Black |

Example: Brown/1/1 = Applicable color wire/ din plug number M12 x 1 pin number/M12 integral cable color wire

Voltage output, 3 wire

+ Output

- Common

Output

Power Supply

+ Supply

4 mA to 20 mA Output Only Vmin = 10V + (.020 x RL) RL	= RS + RW

RL	= Loop Resistance (Ωs) RS	= Sense Resistance (Ωs) RW	= Wire Resistance (Ωs)

| Series 800 | 4 mA to 20 mA 2-wire |
| --- | --- |
| + Supply | Red/1 |
| +Output | Black/2 |

| Series 800 | Voltage Output |
| --- | --- |
| + Supply | Red/1 |
| Common | Black/2 |
| +Output | White/3 |

Example: Red/1 = Applicable color wire/din plug number.

##### 123

Frequently Asked Questions - Dial Indicating  Pressure Gauges

Q: What is the purpose of the ventable & non-ventable fill plug/relief plug?

A: A fill plug seals the fill hole in a pressure gauge case. On liquid filled pressure gauges, a ventable fill plug is used to relieve internal case pressures that occur due to thermal expansion of the fill fluid. In non-filled dry gauges, a non-ventable fill plug is used to occasionally drain the interior of the case from condensate or relieve internal case pressures. Ventable fill plugs incorporate a vent pin to open and close a hole for relieving internal case pressures and do not have to be removed from the case hole like non-ventable fill plugs.

Q: What are the designed overpressure ratings for NOSHOK gauges?

A: Overpressure ratings are specific to the gauge type, pressure range and accuracy ratings of the gauge. Normal overpressure protection can range from 1.1X to 1.3X depending on the gauge selected. NOSHOK gauges comply to the EN-837-1 and ASME B40.1 standards in regards to overpressure protection. When selecting a pressure gauge, it is recommended that the normal system pressure be maintained around half of the full range of the gauge as to avoid overpressure conditions. Overpressure protection of 3 times up to 10 times of the dial range is available on some series as a production option.

Q: How is the accuracy of a gauge affected by a Maximum Indicating Pointer?

A: A Maximum Indicating Pointer (MIP), also commonly referred to as a Tell Tale Pointer, adds an additional ±1% error to the

pressure gauge due to the increase load on the Bourdon tube.

Q: What is a Certified Calibration?

A: Certified Calibrations provide the user with a serial numbered gauge along with a calibration certificate that it has been certified in accordance to the pressure gauge standard with instruments that are traceable to NIST with accuracies of at least 4 to 1.

Q: What is a Certificate of Conformance?

A: A Certificate of Conformance is a formal statement on company letterhead stating that an instrument complies with a particular standard. It contains the signatures of the required personnel. These Certificates are often needed to show industry inspectors that a system and its components are in compliance.

Q: How often does a gauge need to be calibrated?

A: NOSHOK pressure gauges require little or no calibration within the Warranty period. Some applications may be more aggressive than others, resulting in an increased frequency in the need for calibration. The environmental limitations for the pressure gauge series should be observed in all cases. Gauges used in situations outside these requirements may result in inaccuracies, premature wear and/or failure of the gauge and would require additional maintenance. The frequency of calibration, therefore, is up to the user to judge.

Q: When is it recommended to use an orifice?

A: Orifices are a type of snubber. On pressure systems that have rapidly increasing or decreasing pressure spikes, orifices lessen the effects of these energy pulses by blocking the wave energy using restricted flow. They are recommended in dynamic pressure applications with mild pressure spikes.

Q: When is a diaphragm seal used, and when would you apply a diaphragm seal and capillary?

A: A diaphragm is used to isolate and protect the instrument from the process media. Damaging process media may include corrosives, particulates, temperatures, or any state that is not suitable for direct contact with the measuring element.

Diaphragms indirectly transmit system pressures by segregating the process pressure with a thin flexible membrane that in turn transfers the pressure through a fill fluid to the instrument. Diaphragms are often used in conjunction with capillaries to further distance the instrument from the process media. Capillary tubes transmit the diaphragm fill fluid to the instrument. Capillary tubes come in several lengths and provide the user a means to measure in a remote location and may also act as heat dissipaters in high temperature applications.

Q: What is the purpose of liquid filling a gauge, and in what applications would a liquid filled gauge be used?

A: Primarily, in applications that have vibrations or pulsations, liquid filling enables reading the dial pointer by dampening the movement. Liquid filling should be considered in any system that has high dynamic operating conditions. In general, liquid filling helps extend the life of a gauge. It reduces damaging resonance induced fracturing, reduces frictional wear, prevents aggressive ambient air from entering, prevents condensation formation, and improves reliability.

Q: How does temperature affect the accuracy of a pressure gauge?

A: Temperature changes affect the stiffness of a Bourdon tube. The stiffness change is produced by a combination of changes in the elastic (Young’s) modulus and a change in linear dimensions due to linear expansion and contraction. The error caused by temperature change will follow the approximate formula: ± 0.04 x (t2 –t,) % of the span.

124

Frequently Asked Questions - Dial Indicating Pressure Gauges

Q: How do you select a pressure gauge relative to process pressures, normal operating pressures, and maximum

pressures in the process? (Dynamic or static process pressures)

A: The pressure range of a gauge should be 10% over the maximum working pressure in static conditions (no pressure fluctuations). In dynamic conditions, the gauge range should be 40% over the maximum working pressure. Ideally, the pressure gauge range should be selected for a midscale reading during normal operating pressures.

Q: What applications require the various lens materials, and to what maximum temperature can each be subjected?    A: Lens materials include Instrument Glass, Laminated Safety Glass, Tempered Glass, and plastic. Glass lenses are used for abrasion, chemical and wear resistant properties. Laminated Safety Glass reduces the possibility of shattering if the Bourdon tube ruptures. Tempered Glass is 2 to 5 times stronger than Instrument Glass. Plastic lenses are used for impact, corrosion and chemical resistance. Special attention should be paid to the temperature and corrosive environments. Polycarbonate is selected for its superior impact resistance, acrylic for its clarity and scratch resistance and Homalite for is superior chemical resistance.  In general, gauges with plastic lenses should remain below 140° F.

Q: In what situation would a pigtail syphon be used?

A: Pigtail syphons should be used in steam applications and systems that contain superheated vapor. The pigtail buffers the instrument from the damaging effects high temperature steam by holding system fluid in the coil to provide a steam trap for the fluid to condensate and dissipate the heat.

Q: What is the application for a gauge cleaned for O2 service?

A: Oxygen (O2) cleaning is performed on gauges that are used on oxygen service applications. The cleaning removes all hydrocarbons (oil and grease are common hydrocarbons) that can react violently, resulting in explosions, fire, and injury to personnel and property. Oxygen clean gauges can be used in any application that requires the cleanliness level associated with oxygen clean gauge. Glycerin fill gauge cannot be used on oxygen systems.

Q: What fill fluids options are available, and in what applications would each be used?

A: Glycerin is the most common fill fluid. Because of its unique fluid properties, Glycerin has become the standard for liquid filled gauges (see "What is the purpose of liquid filling a gauge?"). Glycerin’s clarity, viscosity, stability, cost, solubility, low toxicity make Glycerin an ideal fluid for many applications. Mineral oils and silicon fluids are used when temperature extremes, chemical compatibility or viscosity fall outside of Glycerin use. Halocarbon® is an inert fluid that is compatible with chlorine, oxygen service, and some high temperature applications. Keep in mind that Glycerin is not compatible with strong oxidizers such as oxygen, chlorine, hydrogen peroxide, or nitric acid. Glycerin & Silicon are explosive in contact with chlorine.

Halocarbon® is explosive in contact with Aluminum and magnesium.

Q: What is the difference between the ASME B40.1 and EN 837-1 specification?

A: The American National Standards Institute (ANSI) approves American National Standards which include the American Society of Mechanical Engineers (ASME) standard ASME B40.100. This Standard (B40.100) is confined to analog, dial-type gauges, which, utilizing elastic elements, mechanically sense pressure and indicate it by means of a pointer moving over a graduated scale. The European Committee for Standardization (CEN) is the officially recognized European standards body that develops European Standards (ENs) which include EN 837-1. The EN 837-1 includes mandatory dimensions, metrology, and testing requirement for sale in the European Union. ASME B40.100 includes similar requirements in a mandatory appendix.

Q: What is the purpose of throttle devices such as throttle plugs and screws?

A: Throttle devices limit the flow to the pressure instrument. They are a type of snubber.

Q: What is the purpose of an over and under load stop in a pressure gauge?

A: The tip motion of a Bourdon tube is translated to rotary motion of a pointer by a linkage and sector gear acting on the pointer pinion gear. Stop pins limit the movement of the Bourdon tube, sector or pointer rotation in over and under pressure conditions that would otherwise move the pointer pinion off the sector gear which would damage the gauge.

125

Frequently Asked Questions - Electronics

- What is the difference between a transducer and transmitter?

  - When these terms originated there was a distinctive difference between the two. A transmitter was referred to as an instrument with a current output signal (i.e. 4 mA to 20 mA) and a transducer was referred to as an instrument with a voltage signal (i.e. 3 mV/V, 0 Vdc to 10 Vdc etc.). As time has progressed these terms are now commonly interchanged for reference to current, voltage and digital output signals.

- What is the difference between the proof pressure and burst pressure specifications?

  - Proof pressure which is higher than the full scale pressure point is the limit that you can go to without affecting the performance

and calibration of the transducer. The burst pressure on the other hand is the limit that you can go before there is pressure chamber rupture and

damage. An overload limit specification used sometimes means that proof and burst ratings are identical.

- Will the series 1800 Attachable Loop Indicator work with transmitters not made by NOSHOK?

  - The series 1800 indicator will work with any brand that has the same pin connections and style Hirschmann connector and sufficient power supply

voltage to drive all instruments in the loop. The series 1800 will use 3 Vdc to operate.

- What does RFI, EMI and ESD mean related to pressure transducers and transmitter?

  - Radio Frequency Interference and Electromagnetic Interference refer to the effects electrical noise can have on instruments. RFI frequently comes from hand held walkie-talkies and EMI comes from AC motors in the vicinity of the instrument.

ESD (Electrostatic Discharge) comes from many sources including the application itself. CE compliant transmitters and transducers incorporate

protection techniques and components to minimize most of the interference.

- Can traditional diaphragm seals or gauge protectors be used with pressure transducers and transmitters?

  - Most diaphragm seals can be used with pressure transducers and transmitters. The real key is to assemble and fill the seal properly, being careful not to entrap air in the fill fluid.

- Are pigtail steam syphons used in transmitter applications?

  - The steam syphon is necessary in steam pressure applications. It is important to isolate the transmitter sensing diaphragm from the high temperature

encountered with steam pressure applications.

- Can orifices and snubbers be used and why would they be needed?

  - As with other pressure measurement instruments including gauges, pressure pulsations and spikes, are issues with pressure transmitters. Whenever the pressure of an incompressible fluid is measured, there is the potential for pulsations and spikes, which can damage pressure transmitters. An orifice installed in the pressure connection by NOSHOK can protect the transmitter from damage. Where there is the possibility of clogging the small orifice, an attachable piston snubber is recommended.

- What is the reason for the vent tube in the cable of the 612 and 627 Series submersible level transmitters?

  - All pressure measurements are inherently differential in theory. Gauge pressure is referenced to ambient atmospheric, absolute pressure is referenced to vacuum contained in an evacuated chamber within the transmitter. The level measurement is also a differential measurement, with its reference to ambient atmospheric pressure. In order for the submersible level measurement to be referenced to atmospheric, the cable contains a vent tube which runs the complete length of the cable and “vents” into the atmospheric pressure at the junction box connection which is out of the liquid.

- How does the series 612 and 627 submersible level transmitter measure level?

  - The transmitter measures the hydrostatic pressure produced by the liquid level higher than the point where the instrument is located. The higher the liquid, the higher the pressure.

- NOSHOK transducers and transmitters are normally 2 wire or 3 wire in output configuration. Is a 4 wire transducer available?

  - Voltage output transducers are available with a 4th connection which is electrically the same as the power supply common to connect to wiring

configurations that require it.

126

Canadian Registration Numbers

CRN documents are available at www.noshok.com.

| Category: F. Measuring Devices |  |
| --- | --- |
| Type of Fitting: | Including pressure gauges, level gauges, sight glasses, level or pressure transmitters |
| Alberta | 0F15217.52 |
| British Columbia | 0F15217.51 |
| Manitoba | 0F15217.54 |
| New Brunswick | 0F15217.57 |
| Newfoundland & Labrador | 0F15217.50 |
| Northwest Territories | 0F15217.5T |
| Nova Scotia | 0F15217.58 |
| Nunavut | 0F15217.5N |
| Ontario | 0F15217.5 |
| Prince Edward Island | 0F15217.59 |
| Quebec | CSA-0F15217.56 |
| Saskatchewan | CSA-0F15217.56 |
| Yukon Territory | 0F15217.5Y |

127

NOTES

128

NOTES

129

NOTES

130

NOTES

131

NOTES

132

NOTES

133

134

NOTES

135

TO DOWNLOAD OR ORDER CATALOGS, VISIT WWW.NOSHOK.COM

# NOSHOK

is committed to providing

a high degree of value and continually improving processes to improve customer satisfaction by focusing on customer requirements for the design, manufacture and distribution of pressure, temperature, and force measurement instruments along with needle and manifold valves including

custom manifold systems for industrial applications.

## And all from a company with a 50+ year record of customer satisfaction.

All from your Single Source Instrumentation Company.

All from world class technology. Combined with real-world stamina.

The highest value with the industry’s best warranty.

###### Corporate Headquarters

1010 West Bagley Road Berea, Ohio 44017

Ph: 440.243.0888

Fax: 440.243.3472

E-mail: noshok@noshok.com

136

Web: www.noshok.com

Catalog NK14PLMS-2